## Job Summary
Final Total ($) | 40910.1781 | Location: | Morningside
Contingency / Client ($) | 958.8323 | Clients: | s360
Margin ($) | 7990.2692 |  | Ascot
Margin (%) | 25%
Contingency / Client (%) | 3%
Summary |  | Total (Hrs) | 234.9933 | Rate | %
Labour | 18939.0667 | Install Labour (Hrs) | 174.5 | 80 | 74.26%
Materials | 13022.01 | Project Management (Hrs) | 13.96 | 80 | 6%
Admin/Overhead | 0 | Site Supervision (Hrs) | 27.92 | 85 | 12%
Additional | 0 | Drafting (Hrs) | 18.6133 | 80 | 8%
Total ($) | 31961.0767
Install Labour ($) | 13960
Project Management ($) | 1116.8
Site Supervision ($) | 2373.2
Drafting ($) | 1489.0667
Material Cost ($) | 11035.3
Continuous Materials Cost ($) | 939.21
Other ($) | 0
Cabling Cost ($) | 1047.5
Additional Mark-up ($) | 0
Project Management ($) | 0
Site Supervision ($) | 0
Drafting ($) | 0
Overhead ($) | 0
Travel/Accommodation ($) | 0

## Sheet1
[8 empty] | Component | Number | Location | Price | Wes Price | 55.57% | Supplier | Component | Wes Price
|  |  | Hr Rate | 80 | [10 empty] | 0 | 0
[15 empty] | 0 | 0
[15 empty] | 0 | 0
| Mech Elect Install Labour | Typical hrs | [12 empty] | 0 | 0
Outdoor Units | CU Unit Roof (or Ground) VRF | 2 | [12 empty] | 0 | 0
| CU Unit - 10 to 20 m cable | 2 | [12 empty] | 0 | 0
| Cabling 10-20m | 2 | [12 empty] | 0 | 0
| CU Unit <1m cable | 0.5 | [12 empty] | 0 | 0
| Cond Unit Sml Dx | 4 | [12 empty] | 0 | 0
Indoor Units | Ducted VRF Unit 10-30m cable | 3.5 | [8 empty] | Sheet1!$B$6:$C$45 |  |  |  | 0 | 0
| Cabling 20-30m | 3.5 | [12 empty] | 0 | 0
| Ducted VRF Unit < 10m | 2.5 | [12 empty] | 0 | 0
| Cassette VRF to CU | 1.5 | [12 empty] | 0 | 0
| Wall VRF Indoor to CU | 0.75 | [12 empty] | 0 | 0
| Branch Box for Heat Recovery | 0.5 | [12 empty] | 0 | 0
| Room VRF to Room DB | 0.5 | [12 empty] | 0 | 0
| Install Catenery | 2 | [12 empty] | 0 | 0
| Install Catenery set out | 1 | [12 empty] | 0 | 0
| Wall Controller VRF | 0.5 | [9 empty] | Stainless switchplate |  |  | 0 | 0
| Wall controller Dx | 0.5 | [12 empty] | 0 | 0
| Central Controller VRF | 4 | [9 empty] | push button switch |  |  | 0 | 0
| Install of Cable tray | 1 | [9 empty] | speed control dial |  |  | 0 | 0
| Fan < 3m cable | 1 | [12 empty] | 0 | 0
| Contactors | 1 | [12 empty] | 0 | 0
| per DOL Fan | 1 | [12 empty] | 0 | 0
| Wall plate to fan OnOff or two speed | 1 | [12 empty] | 0 | 0
| per VSD Fan | 1.5 | [12 empty] | 0 | 0
| per MSSB | 4 | [12 empty] | 0 | 0
| per door or windor reed | 0.5 | [12 empty] | 0 | 0
| Cold room or freeser room | 16 | [12 empty] | 0 | 0
| VRF Network | 0.25 | [12 empty] | 0 | 0
| OAF feed from associated AC | 1 | [12 empty] | 0 | 0
| co sensor | 2 | [12 empty] | 0 | 0
| Control panel | 2 | [12 empty] | 0 | 0
| Commissioning 1hr | 1 | [12 empty] | 0 | 0
| Misc Install - 1hr | 1 | [12 empty] | 0 | 0
| Misc Install - 2hr | 2 | [12 empty] | 0 | 0
| Misc Install - 1.5hr | 1.5 | [12 empty] | 0 | 0
| Misc Install - 2.5hr | 2.5 | [12 empty] | 0 | 0
| 300mm Cable ladder tray install per m | 0.33333 | [12 empty] | 0 | 0
| 80mm Cable ladder tray install per m | 0.13889 | [12 empty] | 0 | 0
| Feed to MSSB from MSB | 0 | [12 empty] | 0 | 0
[15 empty] | 0 | 0
| Nill | 0 | [12 empty] | 0 | 0
[15 empty] | 0 | 0
| Mech Elect Install Hardware | [13 empty] | 0 | 0
| 3 phase isolator 63A WP363 | 38.72 | [5 empty] | 3 phase isolator 63A WP363 | WP363 | B17 | 38.72 | 16 | 58.68% |  | 0 | 0
| RCDBO 10A + GPO Din Mtg | 90.85 | [5 empty] | RCDBO 10A + GPO Din Mtg | DINGPO + RCBO10P1 | B17 / 3B4 | 90.85 | 80 | 11.94% |  | 0 | 0
| 1 phase isolator WP135 | 19.8 | [5 empty] | 1 phase isolator WP135 | WP135 | B17 | 19.8 | 11.8 | 40.4% |  | 0 | 0
| Eureka 60 Pole 400A MS | 6200 | [5 empty] | Eureka 60 Pole 400A MS |  |  |  | 6200 |  |  | 0 | 0
| Eureka 18-42 Pole 250A MS | 3800 | [5 empty] | Eureka 18-42 Pole 250A MS |  |  |  | 3800 |  |  | 0 | 0
| Small Form 1 MSSB ( upto 18 poles) | 488.46 | [5 empty] | Small Form 1 MSSB ( upto 18 poles) |  |  |  | 488.46 |  |  | 0 | 0
| MBO06530 600 x 500 Enclosure, Orange | 294.6 | [5 empty] | MBO06530 600 x 500 Enclosure, Orange | MBO6620 | B53 | 294.6 | 420 | 42.57% |  | 0 | 0
| weather proof enclosure | 0 | [12 empty] | 0 | 0
| CB 3 phase 50A (aprox size) | 36.2 | [5 empty] | CB 3 phase 50A (aprox size) | MCB50P3 | B34 | 36.2 | 17 | 53.04% |  | 0 | 0
| CB Enclosure 12 pole surface | 102 | [5 empty] | CB Enclosure 12 pole surface | MD12WP | B36 | 102 | 22 | 78.43% |  | 0 | 0
| CB 3 Phase 25A | 36.2 | [5 empty] | CB 3 Phase 25A | MCB25P3 | B34 | 36.2 | 17 | 53.04% |  | 0 | 0
| CB 1 Phase 10A | 8.45 | [5 empty] | CB 1 Phase 10A | MCB10P1 | B34 | 8.45 | 4.2 | 50.3% |  | 0 | 0
| Complete Control Panel | 3200 |  |  |  |  | # | Complete Control Panel |  |  |  | 3200 |  |  | Complete Control Panel | 3200
| Reed Sw 15mm barrel | 5 |  |  |  |  | # | Reed Sw 15mm barrel |  |  |  | 5 |  |  | Reed Sw 15mm barrel | 5
| CDIX-400 | 1055 | [5 empty] | CDIX-400 |  |  |  | 1055 |  | Controlstore | 0 | 0
| IO-DIM6 | 65 | [5 empty] | IO-DIM6 |  |  |  | 65 |  | Controlstore | 0 | 0
| GSTA-C | 225 | [5 empty] | GSTA-C |  |  |  | 225 |  | Controlstore | 0 | 0
| CDIB-650 | 1750 | [5 empty] | CDIB-650 |  |  |  | 1750 |  | Controlstore | 0 | 0
| TF63-240-24 | 47 | [5 empty] | TF63-240-24 | TOH63 | B48 | 47 | 100 | 112.8% |  | 0 | 0
| Current Switch CCS131 | 19.5 |  |  |  |  | # | Current Switch CCS131 |  |  |  | 19.5 |  |  | Current Switch CCS131 | 19.5
| QBM2030-1U | 235 |  |  | Design Data |  |  | QBM2030-1U (Differential Pressure Sensor) |  |  |  | 235 |  | Siemens | 0 | 0
| VSD Car Park 1.5kW | 770 | [5 empty] | VSD Car Park 1.5kW |  |  |  | 770 |  | Controlstore | 0 | 0
| VSD Car Park 2.2kW | 550 | [5 empty] | VSD Car Park 2.2kW |  |  |  | 550 |  | Controlstore | 0 | 0
| VSD Car Park 3kW | 750 | [5 empty] | VSD Car Park 3kW |  |  |  | 750 |  | Controlstore | 0 | 0
| VSD Stair Press 7.5kW | 750 | [5 empty] | VSD Stair Press 7.5kW |  |  |  | 750 |  | Controlstore | 0 | 0
| VSD 11 kW | 1100 | [5 empty] | VSD 11 kW |  |  |  | 1100 |  | Controlstore | 0 | 0
| VSD 1.5kW | 770 | [5 empty] | VSD 1.5kW |  |  |  | 770 |  | Controlstore | 0 | 0
| VSD 2.2kW | 750 | [5 empty] | VSD 2.2kW |  |  |  | 750 |  | Controlstore | 0 | 0
| VSD 3kW | 750 | [5 empty] | VSD 3kW |  |  |  | 750 |  | Controlstore | 0 | 0
| VSD 5.5kW | 750 | [5 empty] | VSD 5.5kW |  |  |  | 750 |  | Controlstore | 0 | 0
| VSD 7.5kW | 750 | [5 empty] | VSD 7.5kW |  |  |  | 750 |  | Controlstore | 0 | 0
| 6mm Cable 3 core and Earth | 3.8 | [5 empty] | 6mm Cable 3 core and Earth |  |  |  | 3.8 |  | Design Data | 0 | 0
| 4mm Cable 3 core and Earth | 2.9 | [5 empty] | 4mm Cable 3 core and Earth |  |  |  | 2.9 |  | Design Data | 0 | 0
| Switchboard Cable 1mm | 0.28 | [5 empty] | Switchboard Cable 1mm |  |  |  | 0.28 |  | Design Data | 0 | 0
| 2.5mm Twin and Earth | 0.85 | [5 empty] | 2.5mm Twin and Earth |  |  |  | 0.85 |  | Design Data | 0 | 0
| 7030 2 pair TCAS7302P | 0.88 | [5 empty] | 7030 2 pair TCAS7302P |  |  |  | 0.88 |  | Design Data | 0 | 0
| sheilded cable | 0 | [12 empty] | 0 | 0
| FRC3025+E 2 hour fire for stair p | 4.83 | [5 empty] | FRC3025+E 2 hour fire for stair p |  |  |  | 4.83 |  | Design Data | 0 | 0
| VSD3015E 1.5mm Screened Cable | 3.31 | [5 empty] | VSD3015E 1.5mm Screened Cable |  |  |  | 3.31 |  | Design Data | 0 | 0
| Network cable | 2 | [5 empty] | Network cable |  |  |  | 2 |  | Design Data | 0 | 0
| Caternery 120m per level x 15 | 0.52 | [5 empty] | Caternery 120m per level x 15 |  |  |  | 0.52 |  | Turks | 0 | 0
| Hardware Misc Screws etc per m of cable | 0.5 |  |  |  |  | # | Hardware Misc Screws etc per m of cable |  |  |  | 0.5 |  |  | Hardware Misc Screws etc per m of cable | 0.5
| mech thermostat | 256 | [5 empty] | mech thermostat | ETO6060U |  |  | 256 |  | Controlstore | 0 | 0
| Mech thermostat control relay, control relay, enclosure, terminals etc. | 800 | [5 empty] | Mech thermostat control relay, control relay, enclosure, terminals etc. | ETO6060U |  |  | 800 |  | Controlstore | 0 | 0
| trefolite | 300 | [5 empty] | trefolite |  |  | 300 | 50 | 83.33% |  | 0 | 0
| Wall plates (on off or 2 speed) | 350 |  |  |  |  | # | Wall plates (on off or 2 speed) |  |  |  | 350 |  |  | Wall plates (on off or 2 speed) | 350
| PC Amt stuff | 5000 |  |  |  |  | # | PC Amt stuff |  |  |  | 5000 |  |  | PC Amt stuff | 5000
| AOM Switches | 57.95 | [5 empty] | AOM Switches | RKR22OFO + LEGEND/MOA | B11 | 57.95 | 45 | 22.35% |  | 0 | 0
| 003 Keyed Padlocks | 30 |  |  |  |  | # | 003 Keyed Padlocks |  |  |  | 30 |  |  | 003 Keyed Padlocks | 30
| Cable Tray 225mm wide 2.4mtr | 23 | [5 empty] | Cable Tray 225mm wide 2.4mtr |  |  |  | 23 |  | Turks | 0 | 0
| Cable Tray 80mm wide 2.4mtr | 18 | [5 empty] | Cable Tray 80mm wide 2.4mtr |  |  |  | 18 |  | Turks | 0 | 0
| Cable Tray 80mm wide per metre | 9.75 | [5 empty] | Cable Tray 80mm wide per metre |  |  |  | 9.75 |  | Turks | 0 | 0
| Ladder Tray 300mm wid 2.4mtr | 180 | [5 empty] | Ladder Tray 300mm wid 2.4mtr |  |  |  | 180 |  | Turks | 0 | 0
| Ladder Tray 300mm wid per metre | 97.5 | [5 empty] | Ladder Tray 300mm wid per metre |  |  |  | 97.5 |  | Turks | 0 | 0
| Catenery/Conduit per metre | 1 | [5 empty] | Catenery/Conduit per metre |  |  |  | 1 |  | Turks | 0 | 0
| run and fault leds | 16 | [5 empty] | run and fault leds | PL22G24LED + PL22R24LED | B8 | 16 | 30 | 87.5% |  | 0 | 0
| Stair press sensor | 100 |  |  |  |  | # | Stair press sensor |  |  |  | 100 |  |  | Stair press sensor | 100
| Tubing - 1m | 0 | [12 empty] | 0 | 0
| Air Pressure switch | 50 |  |  |  |  | # | Air Pressure switch |  |  |  | 50 |  |  | Air Pressure switch | 50
| Strobe-alarm | 106 | [5 empty] | Strobe-alarm | SYF13DC24R | B12 | 106 | 100 | 5.66% |  | 0 | 0
| Interface for fire trade fan control | 40 |  |  |  |  | # | Interface for fire trade fan control |  |  |  | 40 |  |  | Interface for fire trade fan control | 40
| Fire Relay | 24.2 | [5 empty] | Fire Relay | 882DC24SLS or 882DC12SLS | B30 | 24.2 | 30 | 23.97% |  | 0 | 0
| General Relay | 24.2 | [5 empty] | General Relay | 882DC24SLS or 882DC12SLS | B30 | 24.2 | 30 | 23.97% |  | 0 | 0
| Control box - Plastic | 50 |  |  |  |  | # | Control box - Plastic |  |  |  | 50 |  |  | Control box - Plastic | 50
| Reed Switch | 50 |  |  |  |  | # | Reed Switch |  |  |  | 50 |  |  | Reed Switch | 50
| Controls transformer | 47 |  |  |  | 540 |  | Controls transformer | TOH63 | B48 | 47 | 50 | 6.383% |  | 0 | 0
| Stainless switchplate - 4 switches | 350 |  |  |  | 135 | # | Stainless switchplate - 4 switches |  |  |  | 350 |  |  | Stainless switchplate - 4 switches | 350
| push button switch | 9.55 | [5 empty] | push button switch | PBF22B | B7 | 9.55 | 30 | 214.1% |  | 0 | 0
| speed control dial | 30 |  |  |  |  | # | speed control dial |  |  |  | 30 |  |  | speed control dial | 30
| SSR ( 1 phase) | 50 |  |  |  |  | # | SSR ( 1 phase) |  |  |  | 50 |  | FASTRON | SSR ( 1 phase) | 50
| SSR (3 phase) | 270 |  |  |  |  | # | SSR (3 phase) |  |  |  | 270 |  | FASTRON | SSR (3 phase) | 270
| Programable Timeclock controller | 80 |  |  |  |  | # | Programable Timeclock controller |  |  |  | 80 |  |  | Programable Timeclock controller | 80
| Run on timer | 50 |  |  |  |  | # | Run on timer |  |  |  | 50 |  |  | Run on timer | 50
| Motion sensor with run on timer | 200 |  |  |  |  | # | Motion sensor with run on timer |  |  |  | 200 |  |  | Motion sensor with run on timer | 200
| HPT | 150 |  |  |  |  | # | HPT |  |  |  | 150 |  |  | HPT | 150
| Spring return damper actuator | 200 |  |  |  |  | # | Spring return damper actuator |  |  |  | 200 |  |  | Spring return damper actuator | 200
| Contactors + OL | 91.05 |  |  |  |  | # | Contactors + OL | CDC1712AC 24vac 10a + CDR17A2.2 |  | 91.05 | 120 | 31.8% |  | Contactors + OL | 120
Hardware Total
|  | Project Total Cost |  |  | 221848.4
|  | Project MU |  |  | 25%
|  | Project Sell |  |  | 277310.5

## Takeoffs
1 |  | Labour cost per hr
2
3
4
5 |  | XXX - IGOC - Rev A.xlsx
6
7
8 | Shopping List | Cost | Markup |  |  |  |  | Sell
9 | Shopping List | 36958.21 | 25% |  |  |  |  | 46197.7625
10
11 | Shopping List | Two CO Detectors per Basement Level | other | [34 empty] | #NAME?
12 | [7 empty] | 46197.7625
13 | [32 empty] | 36958.21
14 | Shopping List | XXX - IGOC - Rev A.xlsx | [31 empty] | Sell Price ( Excluding GST)
15 | Shopping List | [5 empty] | - | 2018-04-26 13:24 | [24 empty] | 46197.7625 |  | 26982.01 | 13960 | 11035.3 | 939.21 | 0 | 0 | 1047.5
16 | Shopping List | Item | Power Supply |  |  |  | QTY | Inclusions | Our Cost - DO NOT SEND | Exclusions | Number off systems | System Description | Inclusions | Cost per system |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | Cost Per System | Labour | Materials | Continous Materials Const. | Other | Additional Markup | Cabling Cost
17 | Shopping List | [5 empty] | 0 | MSSBs |  | MSSBs | [23 empty] | 0
18 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item
19 | [9 empty] | Zero | 0 | large-sized weatherproof CHILLER MSSB | Electrical services for | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
20 | [11 empty] | Item 1 | Main switch , Multifunction Meter, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
21 | [11 empty] | Item 2 | contactors |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
22 | [11 empty] | Item 3 | circuit breakers |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
23 | [11 empty] | Item 4 | busbar and wiring |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
24 | [11 empty] | Item 5 | trefolyte labelling |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
25 | [11 empty] | Item 6 | miscellaneous items |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
26 | [11 empty] | Item 7 | testing |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
27 | [11 empty] | Item 8 | escutcheon plate (to retain IP rating for mounting of lights and switches), |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
28 | [11 empty] | Item 9 | inside powder coated enclosure. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
29 | [11 empty] | Item 10 | Please Note: Chiller MSSB is a specialist custom made system including required components for chiller power supply. Details to be determined following consultants detailed design. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
30 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
31 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
32 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
33 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
34 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
35 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
36 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
37 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
38 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
39 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
40 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
41 | Shopping List | large-sized weatherproof CHILLER MSSB | MSSB |  |  | 1 |  | Electrical services for Zero (0) large-sized weatherproof CHILLER MSSB. This includes supply and install of Main switch , Multifunction Meter, contactors circuit breakers busbar and wiring trefolyte labelling miscellaneous items testing escutcheon plate (to retain IP rating for mounting of lights and switches), inside powder coated enclosure. Please Note: Chiller MSSB is a specialist custom made system including required components for chiller power supply. Details to be determined following consultants detailed design. | 0 |  | Price Check Summary: | large-sized weatherproof CHILLER MSSB | Average cost per system | 15500 |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
42 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
43 | [9 empty] | Zero | 0 | large-sized weatherproof MSSB | Electrical services for | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
44 | [11 empty] | Item 1 | Main switch , Multifunction Meter, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
45 | [11 empty] | Item 2 | contactors |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
46 | [11 empty] | Item 3 | circuit breakers |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
47 | [11 empty] | Item 4 | busbar and wiring |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
48 | [11 empty] | Item 5 | trefolyte labelling |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
49 | [11 empty] | Item 6 | miscellaneous items |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
50 | [11 empty] | Item 7 | testing |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
51 | [11 empty] | Item 8 | escutcheon plate (to retain IP rating for mounting of lights and switches), |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
52 | [11 empty] | Item 9 | inside powder coated enclosure. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
53 | [11 empty] | Item 10 | Please note: MSSB includes other components listed under each system type. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
54 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
55 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
56 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
57 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
58 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
59 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
60 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
61 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
62 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
63 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
64 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
65 | Shopping List | large-sized weatherproof MSSB | MSSB |  |  |  |  | Electrical services for Zero (0) large-sized weatherproof MSSB. This includes supply and install of Main switch , Multifunction Meter, contactors circuit breakers busbar and wiring trefolyte labelling miscellaneous items testing escutcheon plate (to retain IP rating for mounting of lights and switches), inside powder coated enclosure. Please note: MSSB includes other components listed under each system type. | 0 |  | Price Check Summary: | large-sized weatherproof MSSB | Average cost per system | 6700 |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
66 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
67 | [9 empty] | Zero | 0 | medium-sized Form 3 MSSB | Electrical services for | By | Exclusions |  | 0 | per MSSB | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
68 | [11 empty] | Item 1 | Main switch , Multifunction Meter, |  |  |  | 0 | Nill | 0 | 0 | Small Form 1 MSSB ( upto 18 poles) | 488.46 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
69 | [11 empty] | Item 2 | contactors |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
70 | [11 empty] | Item 3 | circuit breakers |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
71 | [11 empty] | Item 4 | busbar and wiring |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
72 | [11 empty] | Item 5 | trefolyte labelling |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
73 | [11 empty] | Item 6 | miscellaneous items |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
74 | [11 empty] | Item 7 | testing |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
75 | [11 empty] | Item 8 | escutcheon plate (to retain IP rating for mounting of lights and switches), |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
76 | [11 empty] | Item 9 | inside powder coated enclosure. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
77 | [11 empty] | Item 10 | Please note: MSSB includes other components listed under each system type. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
78 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
79 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
80 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
81 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
82 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
83 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
84 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
85 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
86 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
87 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
88 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
89 | Shopping List | medium-sized Form 3 MSSB | MSSB |  |  | 2 |  | Electrical services for Zero (0) medium-sized Form 3 MSSB. This includes supply and install of Main switch , Multifunction Meter, contactors circuit breakers busbar and wiring trefolyte labelling miscellaneous items testing escutcheon plate (to retain IP rating for mounting of lights and switches), inside powder coated enclosure. Please note: MSSB includes other components listed under each system type. | 0 |  | Price Check Summary: | medium-sized Form 3 MSSB | Average cost per system | 4300 |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
90 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
91 | [9 empty] | Zero | 0 | medium-sized 316 S/S Form 2 MSSB | Electrical services for | By | Exclusions |  | 0 | per MSSB | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
92 | [11 empty] | Item 1 | Main switch, |  |  |  | 0 | Nill | 0 | 0 | Small Form 1 MSSB ( upto 18 poles) | 488.46 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
93 | [11 empty] | Item 2 | contactors |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
94 | [11 empty] | Item 3 | circuit breakers |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
95 | [11 empty] | Item 4 | busbar and wiring |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
96 | [11 empty] | Item 5 | trefolyte labelling |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
97 | [11 empty] | Item 6 | miscellaneous items |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
98 | [11 empty] | Item 7 | testing |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
99 | [11 empty] | Item 8 | escutcheon plate (to retain IP rating for mounting of lights and switches), |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
100 | [11 empty] | Item 9 | inside powder coated enclosure. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
101 | [11 empty] | Item 10 | Please note: MSSB includes other components listed under each system type. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
102 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
103 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
104 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
105 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
106 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
107 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
108 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
109 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
110 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
111 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
112 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
113 | Shopping List | medium-sized 316 S/S Form 2 MSSB | MSSB | 1 | 1 |  |  | Electrical services for Zero (0) medium-sized 316 S/S Form 2 MSSB. This includes supply and install of Main switch, contactors circuit breakers busbar and wiring trefolyte labelling miscellaneous items testing escutcheon plate (to retain IP rating for mounting of lights and switches), inside powder coated enclosure. Please note: MSSB includes other components listed under each system type. | 0 |  | Price Check Summary: | medium-sized 316 S/S Form 2 MSSB | Average cost per system | 8600 |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
114 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
115 | [9 empty] | Zero | 0 | medium-sized Form 2 MSSB | Electrical services for | By | Exclusions |  | 0 | per MSSB | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
116 | [11 empty] | Item 1 | Main switch, |  |  |  | 0 | Nill | 0 | 0 | Small Form 1 MSSB ( upto 18 poles) | 488.46 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
117 | [11 empty] | Item 2 | contactors |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
118 | [11 empty] | Item 3 | circuit breakers |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
119 | [11 empty] | Item 4 | busbar and wiring |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
120 | [11 empty] | Item 5 | trefolyte labelling |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
121 | [11 empty] | Item 6 | miscellaneous items |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
122 | [11 empty] | Item 7 | testing |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
123 | [11 empty] | Item 8 | escutcheon plate (to retain IP rating for mounting of lights and switches), |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
124 | [11 empty] | Item 9 | inside powder coated enclosure. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
125 | [11 empty] | Item 10 | Please note: MSSB includes other components listed under each system type. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
126 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
127 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
128 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
129 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
130 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
131 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
132 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
133 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
134 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
135 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
136 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
137 | Shopping List | medium-sized Form 2 MSSB | MSSB | 1 | 1 |  |  | Electrical services for Zero (0) medium-sized Form 2 MSSB. This includes supply and install of Main switch, contactors circuit breakers busbar and wiring trefolyte labelling miscellaneous items testing escutcheon plate (to retain IP rating for mounting of lights and switches), inside powder coated enclosure. Please note: MSSB includes other components listed under each system type. | 0 |  | Price Check Summary: | medium-sized Form 2 MSSB | Average cost per system | 4300 |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
138 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
139 | [9 empty] | Zero | 0 | medium-sized weatherproof Form 1 MSSB | Electrical services for | By | Exclusions |  | 0 | per MSSB | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
140 | [11 empty] | Item 1 | Main switch |  |  |  | 0 | Nill | 0 | 0 | Small Form 1 MSSB ( upto 18 poles) | 488.46 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
141 | [11 empty] | Item 2 | contactors |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
142 | [11 empty] | Item 3 | circuit breakers |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
143 | [11 empty] | Item 4 | busbar and wiring |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
144 | [11 empty] | Item 5 | trefolyte labelling |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
145 | [11 empty] | Item 6 | miscellaneous items |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
146 | [11 empty] | Item 7 | testing |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
147 | [11 empty] | Item 8 | escutcheon plate (to retain IP rating for mounting of lights and switches), |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
148 | [11 empty] | Item 9 | inside powder coated enclosure. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
149 | [11 empty] | Item 10 | Please note: MSSB includes other components listed under each system type. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
150 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
151 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
152 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
153 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
154 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
155 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
156 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
157 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
158 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
159 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
160 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
161 | Shopping List | medium-sized weatherproof Form 1 MSSB | MSSB |  |  |  |  | Electrical services for Zero (0) medium-sized weatherproof Form 1 MSSB. This includes supply and install of Main switch contactors circuit breakers busbar and wiring trefolyte labelling miscellaneous items testing escutcheon plate (to retain IP rating for mounting of lights and switches), inside powder coated enclosure. Please note: MSSB includes other components listed under each system type. | 0 |  | Price Check Summary: | medium-sized weatherproof Form 1 MSSB | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
162 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
163 | [9 empty] | Zero | 0 | medium-sized Form 1 MSSBs | Electrical services for | By | Exclusions |  | 0 | per MSSB | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
164 | [11 empty] | Item 1 | Main switch |  |  |  | 0 | Nill | 0 | 0 | Small Form 1 MSSB ( upto 18 poles) | 488.46 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
165 | [11 empty] | Item 2 | contactors |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
166 | [11 empty] | Item 3 | circuit breakers |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
167 | [11 empty] | Item 4 | busbar and wiring |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
168 | [11 empty] | Item 5 | trefolyte labelling |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
169 | [11 empty] | Item 6 | miscellaneous items |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
170 | [11 empty] | Item 7 | testing |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
171 | [11 empty] | Item 8 | inside powder coated enclosure. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
172 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
173 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
174 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
175 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
176 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
177 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
178 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
179 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
180 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
181 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
182 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
183 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
184 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
185 | Shopping List | medium-sized Form 1 MSSBs | MSSB |  |  |  |  | Electrical services for Zero (0) medium-sized Form 1 MSSBs. This includes supply and install of Main switch contactors circuit breakers busbar and wiring trefolyte labelling miscellaneous items testing inside powder coated enclosure. | 0 |  | Price Check Summary: | medium-sized Form 1 MSSBs | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
186 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
187 | [9 empty] | Zero | 0 | small MSSBs | Electrical services for | By | Exclusions |  | 0 | per MSSB | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
188 | [11 empty] | Item 1 | Main switch |  |  |  | 0 | Nill | 0 | 0 | Small Form 1 MSSB ( upto 18 poles) | 488.46 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
189 | [11 empty] | Item 2 | contactors |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
190 | [11 empty] | Item 3 | circuit breakers |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
191 | [11 empty] | Item 4 | busbar and wiring |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
192 | [11 empty] | Item 5 | trefolyte labelling |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
193 | [11 empty] | Item 6 | miscellaneous items |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
194 | [11 empty] | Item 7 | testing |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
195 | [11 empty] | Item 8 | inside powder coated enclosure. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
196 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
197 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
198 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
199 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
200 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
201 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
202 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
203 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
204 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
205 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
206 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
207 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
208 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
209 | Shopping List | small MSSBs | MSSB |  |  |  |  | Electrical services for Zero (0) small MSSBs. This includes supply and install of Main switch contactors circuit breakers busbar and wiring trefolyte labelling miscellaneous items testing inside powder coated enclosure. | 0 |  | Price Check Summary: | small MSSBs | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
210 | Shopping List | [5 empty] | 17 | Fans |  | Fans | [24 empty] | 0 | 0 | 0 | 0 | 0
211 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
212 | [9 empty] | Zero | 0 | fire pump room fan - from local power supply | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
213 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | per DOL Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
214 | [7 empty] | Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply |  |  |  | Item 2 | cabling to fan and control panel (from Builder's Electrician's isolator) | Builders electrician | local power supply |  | 0 | Fan < 3m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 5 |  |  | 0 | 0 | 0 | 0 | 0
215 | [11 empty] | Item 3 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
216 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
217 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
218 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
219 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
220 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Control panel | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
221 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
222 | [8 empty] | high temp thermostat (for additional safety/redundancy) for fire pump room fan - from local power supply |  |  | Item 10 | high temp thermostat, |  |  | high temp thermostat (for additional safety/redundancy) | 0 | Misc Install - 1hr | 0 | 0 | mech thermostat | 256 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
223 | [11 empty] | Item 11 | current switch and cable to light switch ( to turn system on with lights) |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
224 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
225 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
226 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to status cabling from pumps. |  |  |  | Item 14 | fire relay for interface with fire trade, | Fire trade | status cabling from pumps. |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
227 | [11 empty] | Item 15 | run and fault lights, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
228 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
229 | [8 empty] | Auto/Off/On switch for fire pump room fan - from local power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
230 | [11 empty] | Item 18 | controls enclosure, |  |  |  | 0 | Nill | 0 | 0 | Control box - Plastic | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
231 | [11 empty] | Item 19 | trefolyte labelling |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
232 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
233 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
234 | Shopping List | fire pump room fan - from local power supply | LOCAL |  |  |  |  | Electrical power supply and controls to Zero (0) fire pump room fan - from local power supply. This includes supply and install of power and controls. Power for system includes: cabling to fan and control panel (from Builder's Electrician's isolator) and local isolator. Controls for system includes: high temp thermostat, current switch and cable to light switch ( to turn system on with lights) controls cabling, contactors/relays, fire relay for interface with fire trade, run and fault lights, Auto/Off/On switch, controls enclosure, trefolyte labelling and commissioning/testing. Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply Coordination Note: - Fire trade: Please refer to our exclusions relating to status cabling from pumps. | 0 | local power supply status cabling from pumps. | Price Check Summary: | fire pump room fan - from local power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  | 0 | 0 | 0 | 0 | 0 | 0 | 0
235 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
236 | [9 empty] | eight | 8 | timeclock controlled DOL fan - from local power supply | Electrical power supply and controls to | By | Exclusions |  | 8 | Nill | 8 | 0 | Nill | 0 | 0 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
237 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 8 | per DOL Fan | 8 | 8 | Nill | 0 | 0 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
238 | [7 empty] | Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply |  |  |  | Item 2 | cabling to fan and control panel (from Builder's Electrician's isolator) | Builders electrician | local power supply |  | 8 | Fan < 3m cable | 8 | 8 | Nill | 0 | 0 | 8 | 8 | 1 | 4mm Cable 3 core and Earth | 2.9 | 116 | 40 | 8 | 5 |  |  | 0 | 0 | 0 | 0 | 0
239 | [11 empty] | Item 3 | and local isolator. |  |  |  | 8 | Nill | 8 | 0 | 3 phase isolator 63A WP363 | 38.72 | 309.76 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
240 | [11 empty] | Item 4 |  |  |  |  | 8 | Nill | 8 | 0 | Nill | 0 | 0 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
241 | [11 empty] | Item 5 |  |  |  |  | 8 | Nill | 8 | 0 | Nill | 0 | 0 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
242 | [11 empty] | Item 6 |  |  |  |  | 8 | Nill | 8 | 0 | Nill | 0 | 0 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
243 | [11 empty] | Item 7 |  |  |  |  | 8 | Nill | 8 | 0 | Nill | 0 | 0 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
244 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 8 | Control panel | 8 | 16 | Nill | 0 | 0 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
245 | [11 empty] | Item 9 |  |  |  |  | 8 | Nill | 8 | 0 | Nill | 0 | 0 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
246 | [11 empty] | Item 10 | timeclock, |  |  |  | 8 | Misc Install - 1hr | 8 | 8 | Programable Timeclock controller | 80 | 640 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
247 | [11 empty] | Item 11 |  |  |  |  | 8 | Nill | 8 | 0 | Nill | 0 | 0 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
248 | [11 empty] | Item 12 | controls cabling, |  |  |  | 8 | Nill | 8 | 0 | Nill | 0 | 0 | 8 | 8 | 1 | 7030 2 pair TCAS7302P | 0.88 | 211.2 | 240 | 8 | 30 |  |  | 0 | 0 | 0 | 0 | 0
249 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 8 | Contactors | 8 | 8 | Contactors + OL | 91.05 | 728.4 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
250 | [11 empty] | Item 14 |  |  |  |  | 8 | Nill | 8 | 0 | Nill | 0 | 0 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
251 | [8 empty] | run and fault lights for timeclock controlled DOL fan - from local power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 8 | Nill | 8 | 0 | run and fault leds | 16 | 256 | 16 | 8 | 2 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
252 | [11 empty] | Item 16 |  |  |  |  | 8 | Nill | 8 | 0 | Nill | 0 | 0 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
253 | [8 empty] | Auto/Off/On switch for timeclock controlled DOL fan - from local power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 8 | Nill | 8 | 0 | AOM Switches | 57.95 | 463.6 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
254 | [11 empty] | Item 18 | controls enclosure, |  |  |  | 8 | Nill | 8 | 0 | Control box - Plastic | 50 | 400 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
255 | [11 empty] | Item 19 | trefolyte labelling |  |  |  | 8 | Nill | 8 | 0 | Controls transformer | 47 | 376 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
256 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 8 | Commissioning 1hr | 8 | 8 | Nill | 0 | 0 | 8 | 8 | 1 | Nill | 0 | 0 | 0 | 8 | 0 |  |  | 0 | 0 | 0 | 0 | 0
257 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 7980.96 |  |  |  | Total Labour Cost | 4480 | 56 | Total Materials item 1 cost |  | 3173.76 |  |  |  | Total continuous material cost |  | 327.2 |  |  |  | 7980.96 |  | 0 | 0 | 0 | 0 | 0
258 | Shopping List | timeclock controlled DOL fan - from local power supply | LOCAL |  |  |  | 8 | Electrical power supply and controls to eight (8) timeclock controlled DOL fan - from local power supply. Each includes supply and install of power and controls. Power for system includes: cabling to fan and control panel (from Builder's Electrician's isolator) and local isolator. Controls for system includes: timeclock, controls cabling, contactors/relays, run and fault lights, Auto/Off/On switch, controls enclosure, trefolyte labelling and commissioning/testing. Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply | 7980.96 | local power supply | Price Check Summary: | timeclock controlled DOL fan - from local power supply | Average cost per system | 997.62 |  |  |  | Average hrs per system |  | 7 | Average cost per system |  | 396.72 |  |  |  | Average cost per system |  | 40.9 |  |  |  | 9976.2 | 1995.24 | 7980.96 | 4480 | 3173.76 | 327.2 | 0
259 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
260 | [9 empty] | Zero | 0 | temperature controlled fan - from local power supply | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
261 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | per DOL Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
262 | [7 empty] | Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply |  |  |  | Item 2 | cabling to fan and control panel (from Builder's Electrician's isolator) | Builders electrician | local power supply |  | 0 | Fan < 3m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 5 |  |  | 0 | 0 | 0 | 0 | 0
263 | [11 empty] | Item 3 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
264 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
265 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
266 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
267 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
268 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Control panel | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
269 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
270 | [11 empty] | Item 10 | high temp thermostat, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | mech thermostat | 256 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
271 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
272 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 30 |  |  | 0 | 0 | 0 | 0 | 0
273 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
274 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
275 | [8 empty] | run and fault lights for temperature controlled fan - from local power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
276 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
277 | [8 empty] | Auto/Off/On switch for temperature controlled fan - from local power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
278 | [11 empty] | Item 18 | controls enclosure, |  |  |  | 0 | Nill | 0 | 0 | Control box - Plastic | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
279 | [11 empty] | Item 19 | trefolyte labelling |  |  |  | 0 | Nill | 0 | 0 | Controls transformer | 47 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
280 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
281 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
282 | Shopping List | temperature controlled fan - from local power supply | LOCAL |  |  |  |  | Electrical power supply and controls to Zero (0) temperature controlled fan - from local power supply. This includes supply and install of power and controls. Power for system includes: cabling to fan and control panel (from Builder's Electrician's isolator) and local isolator. Controls for system includes: high temp thermostat, controls cabling, contactors/relays, run and fault lights, Auto/Off/On switch, controls enclosure, trefolyte labelling and commissioning/testing. Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply | 0 | local power supply | Price Check Summary: | temperature controlled fan - from local power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
283 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
284 | [9 empty] | one | 1 | carpark fan ( excluding controls) | Electrical power supply and controls to | By | Exclusions |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
285 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 1 | per VSD Fan | 1 | 1.5 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0
286 | [11 empty] | Item 2 | CB, |  |  |  | 1 | Nill | 1 | 0 | CB 3 Phase 25A | 36.2 | 36.2 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
287 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 1 | Fan < 3m cable | 1 | 1 | Nill | 0 | 0 | 1 | 1 | 1 | 4mm Cable 3 core and Earth | 2.9 | 4.35 | 1.5 | 1 | 1.5 |  |  | 0 | 0 | 0 | 0 | 0
288 | [11 empty] | Item 4 | Danfoss VSD ( with internal program for stair press control), |  |  |  | 1 | Nill | 1 | 0 | VSD 7.5kW | 750 | 750 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
289 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | FRC3025+E 2 hour fire for stair p | 4.83 | 72.45 | 15 | 1 | 15 |  |  | 0 | 0 | 0 | 0 | 0
290 | [11 empty] | Item 6 | local isolator, |  |  |  | 1 | Nill | 1 | 0 | 3 phase isolator 63A WP363 | 38.72 | 38.72 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
291 | [11 empty] | Item 7 | 003 padlock, |  |  |  | 1 | Nill | 1 | 0 | 003 Keyed Padlocks | 30 | 30 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
292 | [11 empty] | Item 8 | fan isolator and manual controls AS1668.1 trefolyte label. |  |  |  | 1 | Nill | 1 | 0 | trefolite | 300 | 300 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
293 | [11 empty] | Item 9 | Controls for systems includes: |  |  |  | 1 | Misc Install - 2hr | 1 | 2 | Nill | 0 | 0 | 1 | 1 | 1 | FRC3025+E 2 hour fire for stair p | 4.83 | 96.6 | 20 | 1 | 20 |  |  | 0 | 0 | 0 | 0 | 0
294 | [11 empty] | Item 10 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 2 | 1 | 2 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
295 | [11 empty] | Item 11 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
296 | [11 empty] | Item 12 | controls cabling, |  |  |  | 1 | Misc Install - 2hr | 1 | 2 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
297 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 1 | Contactors | 1 | 1 | Contactors + OL | 91.05 | 91.05 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
298 | [11 empty] | Item 14 | air pressure switch, |  |  |  | 1 | Misc Install - 1hr | 1 | 1 | Air Pressure switch | 50 | 50 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
299 | [8 empty] | Run and fault lights for carpark fan ( excluding controls) |  |  | Item 15 | run light, |  |  | Run and fault lights | 1 | Nill | 1 | 0 | run and fault leds | 16 | 16 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
300 | [11 empty] | Item 16 | fault light, |  |  |  | 1 | Nill | 1 | 0 | run and fault leds | 16 | 16 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
301 | [8 empty] | Auto/Off/On switch for carpark fan ( excluding controls) |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 1 | Nill | 1 | 0 | AOM Switches | 57.95 | 57.95 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
302 | [11 empty] | Item 18 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
303 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface for fire trade connection | Fire trade | fire cabling from FIP. |  | 1 | Nill | 1 | 0 | Interface for fire trade fan control | 40 | 40 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
304 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 1 | Misc Install - 2hr | 1 | 2 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
305 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 2439.32 |  |  |  | Total Labour Cost | 840 | 10.5 | Total Materials item 1 cost |  | 1425.92 |  |  |  | Total continuous material cost |  | 173.4 |  |  |  | 2439.32 |  | 0 | 0 | 0 | 0 | 0
306 | Shopping List | carpark fan ( excluding controls) | EITHER |  |  |  | 1 | Electrical power supply and controls to one (1) carpark fan ( excluding controls). This includes supply and install of power and controls. Power for systems includes: CB, cabling to VSD, Danfoss VSD ( with internal program for stair press control), shielded cabling, local isolator, 003 padlock, fan isolator and manual controls AS1668.1 trefolyte label. Controls for systems includes: controls cabling, contactors/relays, air pressure switch, run light, fault light, Auto/Off/On switch, interface for fire trade connection and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 2439.32 | fire cabling from FIP. | Price Check Summary: | carpark fan ( excluding controls) | Average cost per system | 2439.32 |  |  |  | Average hrs per system |  | 10.5 | Average cost per system |  | 1425.92 |  |  |  | Average cost per system |  | 173.4 |  |  |  |  | 609.83 | 2439.32 | 840 | 1425.92 | 173.4 | 0
307 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
308 | [9 empty] | Zero | 0 | substation ventilation system (Including temperature control and alarm) - From local power supply | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
309 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | per DOL Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
310 | [7 empty] | Coordination Note: - Builders Electrician: Please refer to our exclusions relating to substation ventilation power supply (including isolator) |  |  |  | Item 2 | cabling to fan and control panel (from Builder's Electrician's isolator) | Builders Electrician | substation ventilation power supply (including isolator) |  | 0 | Fan < 3m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 5 |  |  | 0 | 0 | 0 | 0 | 0
311 | [11 empty] | Item 3 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
312 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
313 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
314 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
315 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
316 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Control panel | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
317 | [8 empty] | alarm thermostat ( separate to control thermostat to avoid false alarms) for substation ventilation system (Including temperature control and alarm) - From local power supply |  |  | Item 9 | alarm thermostat, |  |  | alarm thermostat ( separate to control thermostat to avoid false alarms) | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
318 | [11 empty] | Item 10 | high temp thermostat, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | mech thermostat | 256 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
319 | [11 empty] | Item 11 | low temp thermostat, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | mech thermostat | 256 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
320 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 30 |  |  | 0 | 0 | 0 | 0 | 0
321 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 3 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
322 | [11 empty] | Item 14 | air flow switch, |  |  |  | 0 | Nill | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
323 | [8 empty] | run and fault lights for substation ventilation system (Including temperature control and alarm) - From local power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
324 | [11 empty] | Item 16 | strobe-alarm, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Strobe-alarm | 106 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
325 | [8 empty] | Auto/Off/On switch for substation ventilation system (Including temperature control and alarm) - From local power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
326 | [11 empty] | Item 18 | controls enclosure, |  |  |  | 0 | Nill | 0 | 0 | Control box - Plastic | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
327 | [11 empty] | Item 19 | controls transformer |  |  |  | 0 | Nill | 0 | 0 | Controls transformer | 47 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
328 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
329 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
330 | Shopping List | substation ventilation system (Including temperature control and alarm) - From local power supply | LOCAL |  |  |  |  | Electrical power supply and controls to Zero (0) substation ventilation system (Including temperature control and alarm) - From local power supply. This includes supply and install of power and controls. Power for system includes: cabling to fan and control panel (from Builder's Electrician's isolator) and local isolator. Controls for system includes: alarm thermostat, high temp thermostat, low temp thermostat, controls cabling, contactors/relays, air flow switch, run and fault lights, strobe-alarm, Auto/Off/On switch, controls enclosure, controls transformer and commissioning/testing. Coordination Note: - Builders Electrician: Please refer to our exclusions relating to substation ventilation power supply (including isolator) | 0 | substation ventilation power supply (including isolator) | Price Check Summary: | substation ventilation system (Including temperature control and alarm) - From local power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
331 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
332 | [9 empty] | Zero | 0 | DOL fan with interlock with mechanical thermostat - from MSSB power supply | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
333 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | per DOL Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
334 | [11 empty] | Item 2 | CB and cabling to fan from MSSB, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | CB 1 Phase 10A | 8.45 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 5 |  |  | 0 | 0 | 0 | 0 | 0
335 | [11 empty] | Item 3 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | 1 phase isolator WP135 | 19.8 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
336 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
337 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
338 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
339 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
340 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Control panel | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
341 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
342 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
343 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
344 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
345 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
346 | [11 empty] | Item 14 | interlock with mechanical thermostat, |  |  |  | 0 | Nill | 0 | 0 | mech thermostat | 256 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
347 | [8 empty] | run and fault lights for DOL fan with interlock with mechanical thermostat - from MSSB power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
348 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
349 | [8 empty] | Auto/Off/On switch for DOL fan with interlock with mechanical thermostat - from MSSB power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
350 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
351 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
352 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
353 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
354 | Shopping List | DOL fan with interlock with mechanical thermostat - from MSSB power supply | MSSB |  |  |  |  | Electrical power supply and controls to Zero (0) DOL fan with interlock with mechanical thermostat - from MSSB power supply. This includes supply and install of power and controls. Power for system includes: CB and cabling to fan from MSSB, and local isolator. Controls for system includes: controls cabling, contactors/relays, interlock with mechanical thermostat, run and fault lights, Auto/Off/On switch, trefolyte labelling, and commissioning/testing. | 0 |  | Price Check Summary: | DOL fan with interlock with mechanical thermostat - from MSSB power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
355 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
356 | [9 empty] | Zero | 0 | Proprietary DOL fan with interlock with Proprietary controller- from MSSB power supply | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
357 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | per DOL Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
358 | [11 empty] | Item 2 | CB and cabling to fan from MSSB, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | CB 1 Phase 10A | 8.45 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 5 |  |  | 0 | 0 | 0 | 0 | 0
359 | [11 empty] | Item 3 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | 1 phase isolator WP135 | 19.8 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
360 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
361 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
362 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
363 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
364 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Control panel | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
365 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
366 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
367 | [7 empty] | Coordination Note: - Proprietary system supplier: Please refer to our exclusions relating to Proprietary controller |  |  |  | Item 11 | installation only of Proprietary controller | Proprietary system supplier | Proprietary controller |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
368 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
369 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
370 | [11 empty] | Item 14 | interlock with associated system, |  |  |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
371 | [8 empty] | run and fault lights for Proprietary DOL fan with interlock with Proprietary controller- from MSSB power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
372 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
373 | [8 empty] | Auto/Off/On switch for Proprietary DOL fan with interlock with Proprietary controller- from MSSB power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
374 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
375 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
376 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
377 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
378 | Shopping List | Proprietary DOL fan with interlock with Proprietary controller- from MSSB power supply | MSSB |  |  |  |  | Electrical power supply and controls to Zero (0) Proprietary DOL fan with interlock with Proprietary controller- from MSSB power supply. This includes supply and install of power and controls. Power for system includes: CB and cabling to fan from MSSB, and local isolator. Controls for system includes: installation only of Proprietary controllercontrols cabling, contactors/relays, interlock with associated system, run and fault lights, Auto/Off/On switch, trefolyte labelling, and commissioning/testing. Coordination Note: - Proprietary system supplier: Please refer to our exclusions relating to Proprietary controller | 0 | Proprietary controller | Price Check Summary: | Proprietary DOL fan with interlock with Proprietary controller- from MSSB power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
379 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
380 | [9 empty] | Zero | 0 | DOL fan with interlock with local switch - from MSSB power supply | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
381 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | per DOL Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
382 | [11 empty] | Item 2 | CB and cabling to fan from MSSB, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | CB 1 Phase 10A | 8.45 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 5 |  |  | 0 | 0 | 0 | 0 | 0
383 | [11 empty] | Item 3 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | 1 phase isolator WP135 | 19.8 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
384 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
385 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
386 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
387 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
388 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Control panel | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
389 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
390 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
391 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
392 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
393 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
394 | [11 empty] | Item 14 | local switch with run light, |  |  |  | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
395 | [8 empty] | run and fault lights for DOL fan with interlock with local switch - from MSSB power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
396 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
397 | [8 empty] | Auto/Off/On switch for DOL fan with interlock with local switch - from MSSB power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
398 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
399 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
400 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
401 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
402 | Shopping List | DOL fan with interlock with local switch - from MSSB power supply | MSSB |  |  |  |  | Electrical power supply and controls to Zero (0) DOL fan with interlock with local switch - from MSSB power supply. This includes supply and install of power and controls. Power for system includes: CB and cabling to fan from MSSB, and local isolator. Controls for system includes: controls cabling, contactors/relays, local switch with run light, run and fault lights, Auto/Off/On switch, trefolyte labelling, and commissioning/testing. | 0 |  | Price Check Summary: | DOL fan with interlock with local switch - from MSSB power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
403 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
404 | [9 empty] | Zero | 0 | DOL fan with interlock with reed switch - from MSSB power supply | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
405 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | per DOL Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
406 | [11 empty] | Item 2 | CB and cabling to fan from MSSB, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | CB 1 Phase 10A | 8.45 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 5 |  |  | 0 | 0 | 0 | 0 | 0
407 | [11 empty] | Item 3 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | 1 phase isolator WP135 | 19.8 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
408 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
409 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
410 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
411 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
412 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Control panel | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
413 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
414 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
415 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
416 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
417 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
418 | [11 empty] | Item 14 | interlock with associated system, |  |  |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
419 | [8 empty] | run and fault lights for DOL fan with interlock with reed switch - from MSSB power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
420 | [11 empty] | Item 16 | reed switch, |  |  |  | 0 | Nill | 0 | 0 | Reed Switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
421 | [8 empty] | Auto/Off/On switch for DOL fan with interlock with reed switch - from MSSB power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
422 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
423 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
424 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
425 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
426 | Shopping List | DOL fan with interlock with reed switch - from MSSB power supply | MSSB |  |  |  |  | Electrical power supply and controls to Zero (0) DOL fan with interlock with reed switch - from MSSB power supply. This includes supply and install of power and controls. Power for system includes: CB and cabling to fan from MSSB, and local isolator. Controls for system includes: controls cabling, contactors/relays, interlock with associated system, run and fault lights, reed switch, Auto/Off/On switch, trefolyte labelling, and commissioning/testing. | 0 |  | Price Check Summary: | DOL fan with interlock with reed switch - from MSSB power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
427 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
428 | [9 empty] | Zero | 0 | DOL fan with interlock - from MSSB power supply | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
429 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | per DOL Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
430 | [11 empty] | Item 2 | CB and cabling to fan from MSSB, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | CB 1 Phase 10A | 8.45 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 5 |  |  | 0 | 0 | 0 | 0 | 0
431 | [11 empty] | Item 3 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | 1 phase isolator WP135 | 19.8 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
432 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
433 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
434 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
435 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
436 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Control panel | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
437 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
438 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
439 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
440 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
441 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
442 | [11 empty] | Item 14 | interlock with associated system, |  |  |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
443 | [8 empty] | run and fault lights for DOL fan with interlock - from MSSB power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
444 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
445 | [8 empty] | Auto/Off/On switch for DOL fan with interlock - from MSSB power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
446 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
447 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
448 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
449 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
450 | Shopping List | DOL fan with interlock - from MSSB power supply | MSSB |  |  |  |  | Electrical power supply and controls to Zero (0) DOL fan with interlock - from MSSB power supply. This includes supply and install of power and controls. Power for system includes: CB and cabling to fan from MSSB, and local isolator. Controls for system includes: controls cabling, contactors/relays, interlock with associated system, run and fault lights, Auto/Off/On switch, trefolyte labelling, and commissioning/testing. | 0 |  | Price Check Summary: | DOL fan with interlock - from MSSB power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
451 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
452 | [9 empty] | Zero | 0 | general fan with interlock - from MSSB power supply ( field wiring outside MSSB by customer) | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
453 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
454 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Power cabling from MSSB to fan. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  |  |  | Item 2 | CB, | Customers in-house electrician | Power cabling from MSSB to fan. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  | 0 | Nill | 0 | 0 | CB 1 Phase 10A | 8.45 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
455 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to and local power isolator ( adjacent to fan). |  |  |  | Item 3 |  | Customers in-house electrician | and local power isolator ( adjacent to fan). |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
456 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to proprietary air-conditioning controllers supply and installation. |  |  |  | Item 4 |  | Customers in-house electrician | proprietary air-conditioning controllers supply and installation. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
457 | [11 empty] | Item 5 | connections of power cabling into MSSB, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
458 | [11 empty] | Item 6 | testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence), |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
459 | [11 empty] | Item 7 | Documented test results of final electrical systems and Form 16 certification. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
460 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Control panel | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
461 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
462 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
463 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
464 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
465 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
466 | [11 empty] | Item 14 | interlock with associated system, |  |  |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
467 | [11 empty] | Item 15 | run and fault lights, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
468 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
469 | [11 empty] | Item 17 | Auto/Off/On switch, |  |  |  | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
470 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
471 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
472 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
473 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
474 | Shopping List | general fan with interlock - from MSSB power supply ( field wiring outside MSSB by customer) | MSSB |  |  |  |  | Electrical power supply and controls to Zero (0) general fan with interlock - from MSSB power supply ( field wiring outside MSSB by customer). This includes supply and install of power and controls. Power for system includes: CB, connections of power cabling into MSSB, testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence), Documented test results of final electrical systems and Form 16 certification. Controls for system includes: controls cabling, contactors/relays, interlock with associated system, run and fault lights, Auto/Off/On switch, trefolyte labelling, and commissioning/testing. Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Power cabling from MSSB to fan. Customers electrician to leave tails adjacent MSSB for Controlworks to connect.Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to and local power isolator ( adjacent to fan). Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to proprietary air-conditioning controllers supply and installation. | 0 | Power cabling from MSSB to fan. Customers electrician to leave tails adjacent MSSB for Controlworks to connect.and local power isolator ( adjacent to fan). proprietary air-conditioning controllers supply and installation. | Price Check Summary: | general fan with interlock - from MSSB power supply ( field wiring outside MSSB by customer) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
475 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
476 | [9 empty] | Zero | 0 | DOL fan with current switch interlock to other circuit- from local power supply | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
477 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | per DOL Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
478 | [7 empty] | Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply |  |  |  | Item 2 | cabling to fan and control panel (from Builder's Electrician's isolator) | Builders electrician | local power supply |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 5 |  |  | 0 | 0 | 0 | 0 | 0
479 | [11 empty] | Item 3 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | 1 phase isolator WP135 | 19.8 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
480 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
481 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
482 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
483 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
484 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
485 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
486 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
487 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
488 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
489 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
490 | [11 empty] | Item 14 | Current switch an interlock with other circuit ( note current switch ensures clear demarcation between trades), |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
491 | [8 empty] | run and fault lights for DOL fan with current switch interlock to other circuit- from local power supply |  |  | Item 15 |  |  |  | run and fault lights | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
492 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | General Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
493 | [8 empty] | Auto/Off/On switch for DOL fan with current switch interlock to other circuit- from local power supply |  |  | Item 17 |  |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
494 | [11 empty] | Item 18 | controls enclosure, |  |  |  | 0 | Nill | 0 | 0 | Control box - Plastic | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
495 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
496 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
497 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
498 | Shopping List | DOL fan with current switch interlock to other circuit- from local power supply | LOCAL |  |  |  | 0 | Electrical power supply and controls to Zero (0) DOL fan with current switch interlock to other circuit- from local power supply. This includes supply and install of power and controls. Power for system includes: cabling to fan and control panel (from Builder's Electrician's isolator) and local isolator. Controls for system includes: controls cabling, contactors/relays, Current switch an interlock with other circuit ( note current switch ensures clear demarcation between trades), controls enclosure, and commissioning/testing. Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply | 0 | local power supply | Price Check Summary: | DOL fan with current switch interlock to other circuit- from local power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
499 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
500 | [9 empty] | seven | 7 | general fan with interlock to lighting circuit- from local power supply | Electrical power supply and controls to | By | Exclusions |  | 7 | Nill | 7 | 0 | Nill | 0 | 0 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
501 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 7 | per DOL Fan | 7 | 7 | Nill | 0 | 0 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
502 | [7 empty] | Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply |  |  |  | Item 2 | cabling to fan and control panel (from Builder's Electrician's isolator) | Builders electrician | local power supply |  | 7 | Fan < 3m cable | 7 | 7 | Nill | 0 | 0 | 7 | 7 | 1 | 2.5mm Twin and Earth | 0.85 | 29.75 | 35 | 7 | 5 |  |  | 0 | 0 | 0 | 0 | 0
503 | [11 empty] | Item 3 | and local isolator. |  |  |  | 7 | Nill | 7 | 0 | 1 phase isolator WP135 | 19.8 | 138.6 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
504 | [11 empty] | Item 4 |  |  |  |  | 7 | Nill | 7 | 0 | Nill | 0 | 0 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
505 | [11 empty] | Item 5 |  |  |  |  | 7 | Nill | 7 | 0 | Nill | 0 | 0 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
506 | [11 empty] | Item 6 |  |  |  |  | 7 | Nill | 7 | 0 | Nill | 0 | 0 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
507 | [11 empty] | Item 7 |  |  |  |  | 7 | Nill | 7 | 0 | Nill | 0 | 0 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
508 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 7 | Control panel | 7 | 14 | Nill | 0 | 0 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
509 | [11 empty] | Item 9 |  |  |  |  | 7 | Nill | 7 | 0 | Nill | 0 | 0 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
510 | [11 empty] | Item 10 |  |  |  |  | 7 | Nill | 7 | 0 | Nill | 0 | 0 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
511 | [11 empty] | Item 11 |  |  |  |  | 7 | Nill | 7 | 0 | Nill | 0 | 0 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
512 | [11 empty] | Item 12 | controls cabling, |  |  |  | 7 | Nill | 7 | 0 | Nill | 0 | 0 | 7 | 7 | 1 | Switchboard Cable 1mm | 0.28 | 1.96 | 7 | 7 | 1 |  |  | 0 | 0 | 0 | 0 | 0
513 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 7 | Contactors | 7 | 7 | Contactors + OL | 91.05 | 637.35 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
514 | [11 empty] | Item 14 | Current switch an interlock with lighting circuit ( note current switch ensures clear demarcation between trades), |  |  |  | 7 | Nill | 7 | 0 | Fire Relay | 24.2 | 169.4 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
515 | [8 empty] | run and fault lights for general fan with interlock to lighting circuit- from local power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 7 | Nill | 7 | 0 | run and fault leds | 16 | 224 | 14 | 7 | 2 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
516 | [11 empty] | Item 16 |  |  |  |  | 7 | Nill | 7 | 0 | Nill | 0 | 0 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
517 | [8 empty] | Auto/Off/On switch for general fan with interlock to lighting circuit- from local power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 7 | Nill | 7 | 0 | AOM Switches | 57.95 | 405.65 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
518 | [11 empty] | Item 18 | controls enclosure, |  |  |  | 7 | Nill | 7 | 0 | Control box - Plastic | 50 | 350 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
519 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 7 | Nill | 7 | 0 | trefolite | 300 | 2100 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
520 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 7 | Commissioning 1hr | 7 | 7 | Nill | 0 | 0 | 7 | 7 | 1 | Nill | 0 | 0 | 0 | 7 | 0 |  |  | 0 | 0 | 0 | 0 | 0
521 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 7416.71 |  |  |  | Total Labour Cost | 3360 | 42 | Total Materials item 1 cost |  | 4025 |  |  |  | Total continuous material cost |  | 31.71 |  |  |  | 7416.71 |  | 0 | 0 | 0 | 0 | 0
522 | Shopping List | general fan with interlock to lighting circuit- from local power supply | LOCAL |  |  |  | 7 | Electrical power supply and controls to seven (7) general fan with interlock to lighting circuit- from local power supply. Each includes supply and install of power and controls. Power for system includes: cabling to fan and control panel (from Builder's Electrician's isolator) and local isolator. Controls for system includes: controls cabling, contactors/relays, Current switch an interlock with lighting circuit ( note current switch ensures clear demarcation between trades), run and fault lights, Auto/Off/On switch, controls enclosure, trefolyte labelling, and commissioning/testing. Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply | 7416.71 | local power supply | Price Check Summary: | general fan with interlock to lighting circuit- from local power supply | Average cost per system | 1059.53 |  |  |  | Average hrs per system |  | 6 | Average cost per system |  | 575 |  |  |  | Average cost per system |  | 4.53 |  |  |  |  | 1854.1775 | 7416.71 | 3360 | 4025 | 31.71 | 0
523 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
524 | [9 empty] | Zero | 0 | general fan with interlock - from local power supply | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
525 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | per DOL Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
526 | [7 empty] | Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply |  |  |  | Item 2 | cabling to fan and control panel (from Builder's Electrician's isolator) | Builders electrician | local power supply |  | 0 | Fan < 3m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 5 |  |  | 0 | 0 | 0 | 0 | 0
527 | [11 empty] | Item 3 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | 1 phase isolator WP135 | 19.8 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
528 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
529 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
530 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
531 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
532 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Control panel | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
533 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
534 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
535 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
536 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
537 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
538 | [11 empty] | Item 14 | interlock with associated system, |  |  |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
539 | [8 empty] | run and fault lights for general fan with interlock - from local power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
540 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
541 | [8 empty] | Auto/Off/On switch for general fan with interlock - from local power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
542 | [11 empty] | Item 18 | controls enclosure, |  |  |  | 0 | Nill | 0 | 0 | Control box - Plastic | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
543 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
544 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
545 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
546 | Shopping List | general fan with interlock - from local power supply | LOCAL |  |  |  |  | Electrical power supply and controls to Zero (0) general fan with interlock - from local power supply. This includes supply and install of power and controls. Power for system includes: cabling to fan and control panel (from Builder's Electrician's isolator) and local isolator. Controls for system includes: controls cabling, contactors/relays, interlock with associated system, run and fault lights, Auto/Off/On switch, controls enclosure, trefolyte labelling, and commissioning/testing. Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply | 0 | local power supply | Price Check Summary: | general fan with interlock - from local power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
547 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
548 | [9 empty] | Zero | 0 | general fan with fire shutdown - from local power supply | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
549 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | per DOL Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
550 | [7 empty] | Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply |  |  |  | Item 2 | cabling to fan and control panel (from Builder's Electrician's isolator) | Builders electrician | local power supply |  | 0 | Fan < 3m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 5 |  |  | 0 | 0 | 0 | 0 | 0
551 | [11 empty] | Item 3 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | 1 phase isolator WP135 | 19.8 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
552 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
553 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
554 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
555 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
556 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Control panel | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
557 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
558 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
559 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
560 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
561 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
562 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 14 | fire relay for interface with fire trade, | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
563 | [8 empty] | run and fault lights for general fan with fire shutdown - from local power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
564 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
565 | [8 empty] | Auto/Off/On switch for general fan with fire shutdown - from local power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
566 | [11 empty] | Item 18 | controls enclosure, |  |  |  | 0 | Nill | 0 | 0 | Control box - Plastic | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
567 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
568 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
569 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
570 | Shopping List | general fan with fire shutdown - from local power supply | LOCAL |  |  |  |  | Electrical power supply and controls to Zero (0) general fan with fire shutdown - from local power supply. This includes supply and install of power and controls. Power for system includes: cabling to fan and control panel (from Builder's Electrician's isolator) and local isolator. Controls for system includes: controls cabling, contactors/relays, fire relay for interface with fire trade, run and fault lights, Auto/Off/On switch, controls enclosure, trefolyte labelling, and commissioning/testing. Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | local power supply fire cabling from FIP. | Price Check Summary: | general fan with fire shutdown - from local power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
571 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
572 | [9 empty] | one | 1 | DOL fan from local power supply - With local switch and run on timer | Electrical power supply to | By | Exclusions |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
573 | [11 empty] | Item 1 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
574 | [11 empty] | Item 2 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | 2.5mm Twin and Earth | 0.85 | 4.25 | 5 | 1 | 5 |  |  | 0 | 0 | 0 | 0 | 0
575 | [7 empty] | Coordination Note: - Builders electrician: Please refer to our exclusions relating to supply of local power supply. |  |  |  | Item 3 | cabling from local supply, | Builders electrician | supply of local power supply. |  | 1 | Fan < 3m cable | 1 | 1 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
576 | [11 empty] | Item 4 | local switch, |  |  |  | 1 | Nill | 1 | 0 | AOM Switches | 57.95 | 57.95 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
577 | [11 empty] | Item 5 | run on timer, |  |  |  | 1 | Commissioning 1hr | 1 | 1 | Run on timer | 50 | 50 | 1 | 1 | 1 | 7030 2 pair TCAS7302P | 0.88 | 8.8 | 10 | 1 | 10 |  |  | 0 | 0 | 0 | 0 | 0
578 | [11 empty] | Item 6 | enclosure, |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
579 | [11 empty] | Item 7 | local isolator |  |  |  | 1 | Nill | 1 | 0 | Control box - Plastic | 50 | 50 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
580 | [11 empty] | Item 8 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
581 | [11 empty] | Item 9 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
582 | [11 empty] | Item 10 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
583 | [11 empty] | Item 11 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
584 | [11 empty] | Item 12 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
585 | [11 empty] | Item 13 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
586 | [11 empty] | Item 14 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
587 | [11 empty] | Item 15 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 2 | 1 | 2 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
588 | [11 empty] | Item 16 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
589 | [11 empty] | Item 17 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
590 | [11 empty] | Item 18 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
591 | [11 empty] | Item 19 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
592 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
593 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 331 |  |  |  | Total Labour Cost | 160 | 2 | Total Materials item 1 cost |  | 157.95 |  |  |  | Total continuous material cost |  | 13.05 |  |  |  | 331 |  | 0 | 0 | 0 | 0 | 0
594 | Shopping List | DOL fan from local power supply - With local switch and run on timer | LOCAL |  |  |  | 1 | Electrical power supply to one (1) DOL fan from local power supply - With local switch and run on timer. This includes supply and install of cabling from local supply, local switch, run on timer, enclosure, local isolator and commissioning/testing. Coordination Note: - Builders electrician: Please refer to our exclusions relating to supply of local power supply. | 331 | supply of local power supply. | Price Check Summary: | DOL fan from local power supply - With local switch and run on timer | Average cost per system | 331 |  |  |  | Average hrs per system |  | 2 | Average cost per system |  | 157.95 |  |  |  | Average cost per system |  | 13.05 |  |  |  |  | 82.75 | 331 | 160 | 157.95 | 13.05 | 0
595 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
596 | [9 empty] | Zero | 0 | DOL fan from local power supply - With local switch and run status light | Electrical power supply to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
597 | [11 empty] | Item 1 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
598 | [11 empty] | Item 2 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 5 |  |  | 0 | 0 | 0 | 0 | 0
599 | [7 empty] | Coordination Note: - Builders electrician: Please refer to our exclusions relating to supply of local power supply. |  |  |  | Item 3 | cabling from local supply, | Builders electrician | supply of local power supply. |  | 0 | Fan < 3m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
600 | [11 empty] | Item 4 | local switch, |  |  |  | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
601 | [11 empty] | Item 5 | runlight and controls cabling, |  |  |  | 0 | Commissioning 1hr | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
602 | [11 empty] | Item 6 | current switch mounted in enclosure, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
603 | [11 empty] | Item 7 | local isolator |  |  |  | 0 | Nill | 0 | 0 | Control box - Plastic | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
604 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
605 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
606 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
607 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
608 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
609 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
610 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
611 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
612 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
613 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
614 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
615 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
616 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
617 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
618 | Shopping List | DOL fan from local power supply - With local switch and run status light | LOCAL |  |  |  | 0 | Electrical power supply to Zero (0) DOL fan from local power supply - With local switch and run status light. This includes supply and install of cabling from local supply, local switch, runlight and controls cabling, current switch mounted in enclosure, local isolator and commissioning/testing. Coordination Note: - Builders electrician: Please refer to our exclusions relating to supply of local power supply. | 0 | supply of local power supply. | Price Check Summary: | DOL fan from local power supply - With local switch and run status light | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
619 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
620 | [9 empty] | Zero | 0 | DOL fan from local power supply | Electrical power supply to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
621 | [11 empty] | Item 1 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
622 | [11 empty] | Item 2 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 5 |  |  | 0 | 0 | 0 | 0 | 0
623 | [7 empty] | Coordination Note: - Builders electrician: Please refer to our exclusions relating to supply of local power supply. |  |  |  | Item 3 | cabling from local supply, | Builders electrician | supply of local power supply. |  | 0 | Fan < 3m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
624 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
625 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
626 | [11 empty] | Item 6 | local isolator |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
627 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
628 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
629 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
630 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
631 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
632 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
633 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
634 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
635 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
636 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
637 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
638 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
639 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
640 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
641 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
642 | Shopping List | DOL fan from local power supply | LOCAL |  |  |  |  | Electrical power supply to Zero (0) DOL fan from local power supply. This includes supply and install of cabling from local supply, local isolator and commissioning/testing. Coordination Note: - Builders electrician: Please refer to our exclusions relating to supply of local power supply. | 0 | supply of local power supply. | Price Check Summary: | DOL fan from local power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
643 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
644 | [9 empty] | Zero | 0 | DOL fan with interlock with lights an run on timer - from MSSB power supply | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
645 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
646 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
647 | [11 empty] | Item 3 | cabling from MSSB, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
648 | [11 empty] | Item 4 |  |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
649 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
650 | [11 empty] | Item 6 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
651 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
652 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
653 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
654 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
655 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
656 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
657 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
658 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 14 | fire relay for interface with fire trade, | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
659 | [8 empty] | run and fault lights for DOL fan with interlock with lights an run on timer - from MSSB power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
660 | [11 empty] | Item 16 | current switch for fan status, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
661 | [8 empty] | Auto/Off/On switch for DOL fan with interlock with lights an run on timer - from MSSB power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
662 | [11 empty] | Item 18 | current switch for lighting interlock, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
663 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
664 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
665 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
666 | Shopping List | DOL fan with interlock with lights an run on timer - from MSSB power supply | MSSB |  |  | 4 |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) DOL fan with interlock with lights an run on timer - from MSSB power supply. This includes supply and install of power and controls. Power for system includes: CB, cabling from MSSB, and local isolator. Controls for system includes: controls cabling, contactors/relays, fire relay for interface with fire trade, run and fault lights, current switch for fan status, Auto/Off/On switch, current switch for lighting interlock, trefolyte labelling, and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | DOL fan with interlock with lights an run on timer - from MSSB power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
667 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
668 | [9 empty] | Zero | 0 | DOL fan with interlock with lights an run on timer - from MSSB power supply and timeclock control | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
669 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
670 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
671 | [11 empty] | Item 3 | cabling from MSSB, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
672 | [11 empty] | Item 4 |  |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
673 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
674 | [11 empty] | Item 6 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
675 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
676 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
677 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
678 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
679 | [11 empty] | Item 11 | adjustable run on timer controller, |  |  |  | 0 | Nill | 0 | 0 | Programable Timeclock controller | 80 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
680 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
681 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
682 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 14 | fire relay for interface with fire trade, | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
683 | [8 empty] | run and fault lights for DOL fan with interlock with lights an run on timer - from MSSB power supply and timeclock control |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
684 | [11 empty] | Item 16 | current switch for fan status, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
685 | [8 empty] | Auto/Off/On switch for DOL fan with interlock with lights an run on timer - from MSSB power supply and timeclock control |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
686 | [11 empty] | Item 18 | current switch for lighting interlock, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
687 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
688 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
689 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
690 | Shopping List | DOL fan with interlock with lights an run on timer - from MSSB power supply and timeclock control | MSSB |  |  | 4 |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) DOL fan with interlock with lights an run on timer - from MSSB power supply and timeclock control. This includes supply and install of power and controls. Power for system includes: CB, cabling from MSSB, and local isolator. Controls for system includes: adjustable run on timer controller, controls cabling, contactors/relays, fire relay for interface with fire trade, run and fault lights, current switch for fan status, Auto/Off/On switch, current switch for lighting interlock, trefolyte labelling, and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | DOL fan with interlock with lights an run on timer - from MSSB power supply and timeclock control | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
691 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
692 | [9 empty] | Zero | 0 | DOL timeclock controlled fan with fire shutdown - from MSSB power supply and | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
693 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
694 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
695 | [11 empty] | Item 3 | cabling from MSSB, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
696 | [11 empty] | Item 4 |  |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
697 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
698 | [11 empty] | Item 6 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
699 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
700 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
701 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
702 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
703 | [11 empty] | Item 11 | adjustable timeclock controller, |  |  |  | 0 | Nill | 0 | 0 | Programable Timeclock controller | 80 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
704 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
705 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
706 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 14 | fire relay for interface with fire trade, | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
707 | [8 empty] | run and fault lights for DOL timeclock controlled fan with fire shutdown - from MSSB power supply and |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
708 | [11 empty] | Item 16 | current switch for fan status, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
709 | [8 empty] | Auto/Off/On switch for DOL timeclock controlled fan with fire shutdown - from MSSB power supply and |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
710 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
711 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
712 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
713 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
714 | Shopping List | DOL timeclock controlled fan with fire shutdown - from MSSB power supply and | MSSB |  |  | 4 |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) DOL timeclock controlled fan with fire shutdown - from MSSB power supply and. This includes supply and install of power and controls. Power for system includes: CB, cabling from MSSB, and local isolator. Controls for system includes: adjustable timeclock controller, controls cabling, contactors/relays, fire relay for interface with fire trade, run and fault lights, current switch for fan status, Auto/Off/On switch, trefolyte labelling, and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | DOL timeclock controlled fan with fire shutdown - from MSSB power supply and | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
715 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
716 | [9 empty] | Zero | 0 | DOL fan with fire shutdown - from MSSB power supply and timeclock control ( field wiring outside MSSB by customer) | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
717 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
718 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Power cabling from MSSB to fans. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  |  |  | Item 2 | CB, | Customers in-house electrician | Power cabling from MSSB to fans. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
719 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to and local power isolator ( for fan). |  |  |  | Item 3 | connections power cabling into MSSB, | Customers in-house electrician | and local power isolator ( for fan). |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
720 | [11 empty] | Item 4 | testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence), |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
721 | [11 empty] | Item 5 | Documented test results of final electrical systems and Form 16 certification. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
722 | [11 empty] | Item 6 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
723 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
724 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
725 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
726 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
727 | [11 empty] | Item 11 | adjustable timeclock controller, |  |  |  | 0 | Nill | 0 | 0 | Programable Timeclock controller | 80 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
728 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
729 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
730 | [7 empty] | Coordination Note: - fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 14 | fire relay for interface with fire trade, | fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
731 | [8 empty] | run and fault lights for DOL fan with fire shutdown - from MSSB power supply and timeclock control ( field wiring outside MSSB by customer) |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
732 | [11 empty] | Item 16 | current switch for fan status, | 0 |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
733 | [8 empty] | Auto/Off/On switch for DOL fan with fire shutdown - from MSSB power supply and timeclock control ( field wiring outside MSSB by customer) |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
734 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
735 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
736 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
737 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
738 | Shopping List | DOL fan with fire shutdown - from MSSB power supply and timeclock control ( field wiring outside MSSB by customer) | MSSB |  |  |  |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) DOL fan with fire shutdown - from MSSB power supply and timeclock control ( field wiring outside MSSB by customer). This includes supply and install of power and controls. Power for system includes: CB, connections power cabling into MSSB, testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence), Documented test results of final electrical systems and Form 16 certification. and local isolator. Controls for system includes: adjustable timeclock controller, controls cabling, contactors/relays, fire relay for interface with fire trade, run and fault lights, current switch for fan status, Auto/Off/On switch, trefolyte labelling, and commissioning/testing. Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Power cabling from MSSB to fans. Customers electrician to leave tails adjacent MSSB for Controlworks to connect.Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to and local power isolator ( for fan). Coordination Note: - fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | Power cabling from MSSB to fans. Customers electrician to leave tails adjacent MSSB for Controlworks to connect.and local power isolator ( for fan). fire cabling from FIP. | Price Check Summary: | DOL fan with fire shutdown - from MSSB power supply and timeclock control ( field wiring outside MSSB by customer) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
739 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
740 | [9 empty] | Zero | 0 | 2 speed DOL fan with fire shutdown - from MSSB power supply | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
741 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
742 | [11 empty] | Item 2 | 2xCB, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 2 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
743 | [11 empty] | Item 3 | 2xcabling from MSSB, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
744 | [11 empty] | Item 4 |  |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
745 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
746 | [11 empty] | Item 6 | and 2xlocal isolator. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
747 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
748 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
749 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
750 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
751 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
752 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
753 | [11 empty] | Item 13 | 2Xcontactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
754 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 14 | fire relay for interface with fire trade, | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
755 | [8 empty] | run and fault lights for 2 speed DOL fan with fire shutdown - from MSSB power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
756 | [11 empty] | Item 16 | current switch for fan status, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
757 |  | 5 | [6 empty] | Auto/Off/On switch for 2 speed DOL fan with fire shutdown - from MSSB power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
758 | [11 empty] | Item 18 | Hi/low speed switch |  |  |  | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
759 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
760 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
761 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
762 | Shopping List | 2 speed DOL fan with fire shutdown - from MSSB power supply | MSSB |  |  | 4 |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) 2 speed DOL fan with fire shutdown - from MSSB power supply . This includes supply and install of power and controls. Power for system includes: 2xCB, 2xcabling from MSSB, and 2xlocal isolator. Controls for system includes: controls cabling, 2Xcontactors/relays, fire relay for interface with fire trade, run and fault lights, current switch for fan status, Auto/Off/On switch, Hi/low speed switchtrefolyte labelling, and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | 2 speed DOL fan with fire shutdown - from MSSB power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
763 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
764 | [9 empty] | Zero | 0 | DOL fan with fire shutdown - from MSSB power supply and BMS interface provisions | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
765 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
766 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
767 | [11 empty] | Item 3 | cabling from MSSB, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
768 | [11 empty] | Item 4 |  |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
769 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
770 | [11 empty] | Item 6 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
771 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
772 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
773 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
774 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
775 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
776 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
777 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
778 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 14 | fire relay for interface with fire trade, | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
779 | [8 empty] | run and fault lights for DOL fan with fire shutdown - from MSSB power supply and BMS interface provisions |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
780 | [11 empty] | Item 16 | current switch for fan status, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
781 |  | 5 | [6 empty] | Auto/Off/On switch for DOL fan with fire shutdown - from MSSB power supply and BMS interface provisions |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
782 | [11 empty] | Item 18 | BMS terminals for on/off control, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
783 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
784 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
785 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
786 | Shopping List | DOL fan with fire shutdown - from MSSB power supply and BMS interface provisions | MSSB |  |  | 4 |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) DOL fan with fire shutdown - from MSSB power supply and BMS interface provisions. This includes supply and install of power and controls. Power for system includes: CB, cabling from MSSB, and local isolator. Controls for system includes: controls cabling, contactors/relays, fire relay for interface with fire trade, run and fault lights, current switch for fan status, Auto/Off/On switch, BMS terminals for on/off control, trefolyte labelling, and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | DOL fan with fire shutdown - from MSSB power supply and BMS interface provisions | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
787 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
788 | [9 empty] | Zero | 0 | Fume Cupboard fan ( Excluding supply of VSD and FC controls) - from MSSB power supply | Electrical power supply to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
789 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
790 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
791 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
792 | [7 empty] | Coordination Note: - Fume cupboard specialist: Please refer to our exclusions relating to supply and commissioning of VSD, interconnect cabling between FC and VSD. |  |  |  | Item 4 | electrical connection of VSD ( supplied by others), | Fume cupboard specialist | supply and commissioning of VSD, interconnect cabling between FC and VSD. |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
793 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
794 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
795 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
796 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
797 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
798 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
799 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
800 | [11 empty] | Item 12 | controls cabling between VSD and MSSB, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
801 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
802 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
803 | [8 empty] | run and fault lights for Fume Cupboard fan ( Excluding supply of VSD and FC controls) - from MSSB power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
804 | [11 empty] | Item 16 | current switch for fan status, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
805 | [8 empty] | Auto/Off/On switch for Fume Cupboard fan ( Excluding supply of VSD and FC controls) - from MSSB power supply |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
806 | [11 empty] | Item 18 | BMS terminals for on/off control, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
807 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
808 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
809 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
810 | Shopping List | Fume Cupboard fan ( Excluding supply of VSD and FC controls) - from MSSB power supply | MSSB |  | 2 | 1 |  | Electrical power supply to Zero (0) Fume Cupboard fan ( Excluding supply of VSD and FC controls) - from MSSB power supply. This includes supply and install of power and controls. Power for system includes: CB, cabling to VSD, electrical connection of VSD ( supplied by others), shielded cabling, local isolator, Controls for system includes: controls cabling between VSD and MSSB, contactors/relays, run and fault lights, current switch for fan status, Auto/Off/On switch, BMS terminals for on/off control, trefolyte labelling, and commissioning/testing. Coordination Note: - Fume cupboard specialist: Please refer to our exclusions relating to supply and commissioning of VSD, interconnect cabling between FC and VSD. | 0 | supply and commissioning of VSD, interconnect cabling between FC and VSD. | Price Check Summary: | Fume Cupboard fan ( Excluding supply of VSD and FC controls) - from MSSB power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
811 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
812 | [9 empty] | Zero | 0 | Small sized VSD fan with fire shutdown - from local power supply | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
813 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
814 | [11 empty] | Item 2 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
815 | [7 empty] | Coordination Note: - Builders electrician: Please refer to our exclusions relating to isolator adjacent fan |  |  |  | Item 3 | cabling to VSD ( from builders electricians isolator), | Builders electrician | isolator adjacent fan |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
816 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | per VSD Fan | 0 | 0 | VSD 2.2kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
817 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
818 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
819 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
820 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
821 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
822 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
823 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
824 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
825 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
826 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 14 | fire relay for interface with fire trade, | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
827 | [8 empty] | run and fault lights for Small sized VSD fan with fire shutdown - from local power supply |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
828 | [11 empty] | Item 16 | enclosure, |  |  |  | 0 | Nill | 0 | 0 | Control box - Plastic | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
829 | [8 empty] | Auto/Off/On switch for Small sized VSD fan with fire shutdown - from local power supply |  |  | Item 17 |  |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
830 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
831 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
832 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
833 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
834 | Shopping List | Small sized VSD fan with fire shutdown - from local power supply | LOCAL |  | 2 | 1 |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) Small sized VSD fan with fire shutdown - from local power supply. This includes supply and install of power and controls. Power for system includes: cabling to VSD ( from builders electricians isolator), Danfoss VSD, shielded cabling, local isolator, Controls for system includes: controls cabling, contactors/relays, fire relay for interface with fire trade, run and fault lights, enclosure, trefolyte labelling, and commissioning/testing. Coordination Note: - Builders electrician: Please refer to our exclusions relating to isolator adjacent fanCoordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | isolator adjacent fanfire cabling from FIP. | Price Check Summary: | Small sized VSD fan with fire shutdown - from local power supply | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
835 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
836 | [9 empty] | Zero | 0 | Small sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
837 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
838 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
839 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
840 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | per VSD Fan | 0 | 0 | VSD 2.2kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
841 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
842 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
843 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
844 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
845 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
846 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
847 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
848 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
849 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
850 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 14 | fire relay for interface with fire trade, | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
851 | [8 empty] | run and fault lights for Small sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
852 | [11 empty] | Item 16 | current switch for fan status, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
853 | [8 empty] | Auto/Off/On switch for Small sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
854 | [11 empty] | Item 18 | BMS terminals for on/off control, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
855 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
856 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
857 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
858 | Shopping List | Small sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions | MSSB |  | 2 | 1 |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) Small sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions. This includes supply and install of power and controls. Power for system includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, Controls for system includes: controls cabling, contactors/relays, fire relay for interface with fire trade, run and fault lights, current switch for fan status, Auto/Off/On switch, BMS terminals for on/off control, trefolyte labelling, and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | Small sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
859 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
860 | [9 empty] | Zero | 0 | Medium sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
861 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
862 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
863 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
864 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | per VSD Fan | 0 | 0 | VSD 5.5kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
865 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
866 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
867 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
868 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
869 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
870 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
871 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
872 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
873 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
874 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 14 | fire relay for interface with fire trade, | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
875 | [8 empty] | run and fault lights for Medium sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
876 | [11 empty] | Item 16 | current switch for fan status, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
877 | [8 empty] | Auto/Off/On switch for Medium sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
878 | [11 empty] | Item 18 | BMS terminals for on/off control, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
879 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
880 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
881 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
882 | Shopping List | Medium sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions | MSSB |  |  | 0 |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) Medium sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions. This includes supply and install of power and controls. Power for system includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, Controls for system includes: controls cabling, contactors/relays, fire relay for interface with fire trade, run and fault lights, current switch for fan status, Auto/Off/On switch, BMS terminals for on/off control, trefolyte labelling, and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | Medium sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
883 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
884 | [9 empty] | Zero | 0 | large sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
885 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
886 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
887 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
888 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | per VSD Fan | 0 | 0 | VSD 11 kW | 1100 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
889 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
890 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
891 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
892 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
893 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
894 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
895 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
896 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
897 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
898 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 14 | fire relay for interface with fire trade, | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
899 | [8 empty] | run and fault lights for large sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
900 | [11 empty] | Item 16 | current switch for fan status, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
901 | [8 empty] | Auto/Off/On switch for large sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
902 | [11 empty] | Item 18 | BMS terminals for on/off control, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
903 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
904 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
905 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
906 | Shopping List | large sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions | MSSB |  |  | 0 |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) large sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions. This includes supply and install of power and controls. Power for system includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, Controls for system includes: controls cabling, contactors/relays, fire relay for interface with fire trade, run and fault lights, current switch for fan status, Auto/Off/On switch, BMS terminals for on/off control, trefolyte labelling, and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | large sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
907 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
908 | [9 empty] | Zero | 0 | Cooling tower fan wirh VSD - from MSSB power supply and BMS interface provisions | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
909 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
910 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
911 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
912 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | per VSD Fan | 0 | 0 | VSD 11 kW | 1100 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
913 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
914 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
915 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
916 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
917 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
918 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
919 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
920 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
921 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
922 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
923 | [8 empty] | run and fault lights for Cooling tower fan wirh VSD - from MSSB power supply and BMS interface provisions |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
924 | [11 empty] | Item 16 | current switch for fan status, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
925 | [8 empty] | Auto/Off/On switch for Cooling tower fan wirh VSD - from MSSB power supply and BMS interface provisions |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
926 | [11 empty] | Item 18 | BMS terminals for on/off control, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
927 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
928 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
929 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
930 | Shopping List | Cooling tower fan wirh VSD - from MSSB power supply and BMS interface provisions | MSSB |  |  | 0 |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) Cooling tower fan wirh VSD - from MSSB power supply and BMS interface provisions. This includes supply and install of power and controls. Power for system includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, Controls for system includes: controls cabling, contactors/relays, run and fault lights, current switch for fan status, Auto/Off/On switch, BMS terminals for on/off control, trefolyte labelling, and commissioning/testing. | 0 |  | Price Check Summary: | Cooling tower fan wirh VSD - from MSSB power supply and BMS interface provisions | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
931 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
932 | [9 empty] | Zero | 0 | Large sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
933 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
934 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
935 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
936 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | per VSD Fan | 0 | 0 | VSD 11 kW | 1100 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
937 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
938 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
939 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
940 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
941 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
942 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
943 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
944 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
945 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
946 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 14 | fire relay for interface with fire trade, | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
947 | [8 empty] | run and fault lights for Large sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
948 | [11 empty] | Item 16 | current switch for fan status, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
949 | [8 empty] | Auto/Off/On switch for Large sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
950 | [11 empty] | Item 18 | BMS terminals for on/off control, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
951 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
952 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
953 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
954 | Shopping List | Large sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions | MSSB |  |  | 0 |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) Large sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions. This includes supply and install of power and controls. Power for system includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, Controls for system includes: controls cabling, contactors/relays, fire relay for interface with fire trade, run and fault lights, current switch for fan status, Auto/Off/On switch, BMS terminals for on/off control, trefolyte labelling, and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | Large sized VSD fan with fire shutdown - from MSSB power supply and BMS interface provisions | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
955 | Shopping List | [5 empty] | 0 | Air Conditioning |  | Air Conditioning | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0
956 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
957 | [9 empty] | Zero | 0 | Electric Duct Heater ( 3 phase with SSR's) | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
958 | [11 empty] | Item 1 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
959 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 phase 50A (aprox size) | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
960 | [11 empty] | Item 3 | cabling between MSSB and Heater |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
961 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
962 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
963 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
964 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
965 | [11 empty] | Item 8 | heater trefolyte label. |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
966 | [11 empty] | Item 9 | Controls for systems includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
967 | [7 empty] | Coordination Note: - BMS trade: Please refer to our exclusions relating to cabling from MSSB's to BMS system |  |  |  | Item 10 | SSR and BMS interface to allow modulating control ( 1 per phase), | BMS trade | cabling from MSSB's to BMS system |  | 0 | Nill | 0 | 0 | SSR ( 1 phase) | 50 | 0 | 0 | 0 | 3 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
968 | [11 empty] | Item 11 | heater protection thermostat ( including cabling back to MSSB and interlock relay), |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | HPT | 150 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
969 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
970 | [11 empty] | Item 13 | contactors/relays ( per phase), |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
971 | [11 empty] | Item 14 | interface with ahu air pressure switch, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
972 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
973 | [11 empty] | Item 16 | HPT fault light, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
974 | [7 empty] | Coordination Note: - BMS trade: Please refer to our exclusions relating to cabling from MSSB's to BMS system |  |  |  | Item 17 | BMS terminals for HPT fault indication, | BMS trade | cabling from MSSB's to BMS system |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
975 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
976 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface at MSSB for fire trade connection | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
977 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
978 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
979 | Shopping List | Electric Duct Heater ( 3 phase with SSR's) | MSSB |  |  | 28 |  | Electrical power supply and controls to Zero (0) Electric Duct Heater ( 3 phase with SSR's). This includes supply and install of CB, cabling between MSSB and Heater local isolator, heater trefolyte label. Controls for systems includes: SSR and BMS interface to allow modulating control ( 1 per phase), heater protection thermostat ( including cabling back to MSSB and interlock relay), controls cabling, contactors/relays ( per phase), interface with ahu air pressure switch, HPT fault light, BMS terminals for HPT fault indication, interface at MSSB for fire trade connection and commissioning/testing. Coordination Note: - BMS trade: Please refer to our exclusions relating to cabling from MSSB's to BMS systemCoordination Note: - BMS trade: Please refer to our exclusions relating to cabling from MSSB's to BMS systemCoordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | cabling from MSSB's to BMS systemcabling from MSSB's to BMS systemfire cabling from FIP. | Price Check Summary: | Electric Duct Heater ( 3 phase with SSR's) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
980 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
981 | [9 empty] | Zero | 0 | Chilled Water AHU with 2 x medium VSD ( Dual fan) | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
982 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
983 | [11 empty] | Item 2 | CB ( 2 per system), |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
984 | [11 empty] | Item 3 | cabling to VSD ( 2 per system), |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
985 | [11 empty] | Item 4 | Danfoss VSD ( 2 per system), |  |  |  | 0 | Nill | 0 | 0 | VSD 5.5kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
986 | [11 empty] | Item 5 | shielded cabling ( 2 per system), |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
987 | [11 empty] | Item 6 | local isolator ( 2 per system), |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
988 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | 003 Keyed Padlocks | 30 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
989 | [11 empty] | Item 8 | fan isolator and trefolyte label, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
990 | [11 empty] | Item 9 | Controls for systems includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
991 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
992 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
993 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 30 |  |  | 0 | 0 | 0 | 0 | 0
994 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
995 | [11 empty] | Item 14 | air pressure switch, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
996 | [8 empty] | Run and fault lights for Chilled Water AHU with 2 x medium VSD ( Dual fan) |  |  | Item 15 | run light, |  |  | Run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
997 | [11 empty] | Item 16 | fault light, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
998 | [8 empty] | Auto/Off/On switch for Chilled Water AHU with 2 x medium VSD ( Dual fan) |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
999 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1000 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface at MSSB for fire trade connection | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1001 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1002 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1003 | Shopping List | Chilled Water AHU with 2 x medium VSD ( Dual fan) | MSSB |  |  | 4 |  | Electrical power supply and controls to Zero (0) Chilled Water AHU with 2 x medium VSD ( Dual fan). This includes supply and install of power and controls. Power for systems includes: CB ( 2 per system), cabling to VSD ( 2 per system), Danfoss VSD ( 2 per system), shielded cabling ( 2 per system), local isolator ( 2 per system), fan isolator and trefolyte label, Controls for systems includes: controls cabling, contactors/relays, air pressure switch, run light, fault light, Auto/Off/On switch, interface at MSSB for fire trade connection and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | Chilled Water AHU with 2 x medium VSD ( Dual fan) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1004 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1005 | [9 empty] | Zero | 0 | Chilled Water AHU with medium VSD | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1006 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1007 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1008 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1009 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | Nill | 0 | 0 | VSD 5.5kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1010 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
1011 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1012 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1013 | [11 empty] | Item 8 | fan isolator and MSSB AS1668.1 trefolyte label. |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1014 | [11 empty] | Item 9 | Controls for systems includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1015 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1016 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1017 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 30 |  |  | 0 | 0 | 0 | 0 | 0
1018 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1019 | [11 empty] | Item 14 | air pressure switch, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1020 | [8 empty] | Run and fault lights for Chilled Water AHU with medium VSD |  |  | Item 15 | run light, |  |  | Run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1021 | [11 empty] | Item 16 | fault light, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1022 | [8 empty] | Auto/Off/On switch for Chilled Water AHU with medium VSD |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1023 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1024 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface at MSSB for fire trade connection | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1025 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1026 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1027 | Shopping List | Chilled Water AHU with medium VSD | MSSB |  |  | 7 |  | Electrical power supply and controls to Zero (0) Chilled Water AHU with medium VSD. This includes supply and install of power and controls. Power for systems includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, fan isolator and MSSB AS1668.1 trefolyte label. Controls for systems includes: controls cabling, contactors/relays, air pressure switch, run light, fault light, Auto/Off/On switch, interface at MSSB for fire trade connection and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | Chilled Water AHU with medium VSD | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1028 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1029 | [9 empty] | Zero | 0 | Chilled Water AHU with large VSD | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1030 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1031 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1032 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1033 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | Nill | 0 | 0 | VSD 11 kW | 1100 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1034 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
1035 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1036 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1037 | [11 empty] | Item 8 | fan isolator and MSSB AS1668.1 trefolyte label. |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1038 | [11 empty] | Item 9 | Controls for systems includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1039 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1040 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1041 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 30 |  |  | 0 | 0 | 0 | 0 | 0
1042 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1043 | [11 empty] | Item 14 | air pressure switch, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1044 | [8 empty] | Run and fault lights for Chilled Water AHU with large VSD |  |  | Item 15 | run light, |  |  | Run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1045 | [11 empty] | Item 16 | fault light, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1046 | [8 empty] | Auto/Off/On switch for Chilled Water AHU with large VSD |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1047 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1048 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface at MSSB for fire trade connection | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1049 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1050 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1051 | Shopping List | Chilled Water AHU with large VSD | MSSB |  |  | 7 |  | Electrical power supply and controls to Zero (0) Chilled Water AHU with large VSD. This includes supply and install of power and controls. Power for systems includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, fan isolator and MSSB AS1668.1 trefolyte label. Controls for systems includes: controls cabling, contactors/relays, air pressure switch, run light, fault light, Auto/Off/On switch, interface at MSSB for fire trade connection and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | Chilled Water AHU with large VSD | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1052 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1053 | [9 empty] | Zero | 0 | Chilled Water AHU with small VSD | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1054 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1055 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1056 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1057 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | Nill | 0 | 0 | VSD 2.2kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1058 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
1059 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1060 | [11 empty] | Item 7 | 003 padlock, |  |  |  | 0 | Nill | 0 | 0 | 003 Keyed Padlocks | 30 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1061 | [11 empty] | Item 8 | fan isolator and MSSB AS1668.1 trefolyte label. |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1062 | [11 empty] | Item 9 | Controls for systems includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1063 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1064 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1065 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 30 |  |  | 0 | 0 | 0 | 0 | 0
1066 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1067 | [11 empty] | Item 14 | air pressure switch, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1068 | [8 empty] | Run and fault lights for Chilled Water AHU with small VSD |  |  | Item 15 | run light, |  |  | Run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1069 | [11 empty] | Item 16 | fault light, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1070 | [8 empty] | Auto/Off/On switch for Chilled Water AHU with small VSD |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1071 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1072 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface at MSSB for fire trade connection | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1073 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1074 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1075 | Shopping List | Chilled Water AHU with small VSD | MSSB |  |  |  |  | Electrical power supply and controls to Zero (0) Chilled Water AHU with small VSD. This includes supply and install of power and controls. Power for systems includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, 003 padlock, fan isolator and MSSB AS1668.1 trefolyte label. Controls for systems includes: controls cabling, contactors/relays, air pressure switch, run light, fault light, Auto/Off/On switch, interface at MSSB for fire trade connection and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | Chilled Water AHU with small VSD | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1076 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1077 | [9 empty] | Zero | 0 | Fire essential Chilled Water AHU with VSD | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1078 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1079 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1080 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1081 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | Nill | 0 | 0 | VSD Car Park 3kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1082 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
1083 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1084 | [11 empty] | Item 7 | 003 padlock, |  |  |  | 0 | Nill | 0 | 0 | 003 Keyed Padlocks | 30 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1085 | [11 empty] | Item 8 | fan isolator and MSSB AS1668.1 trefolyte label. |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1086 | [11 empty] | Item 9 | Controls for systems includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1087 | [11 empty] | Item 10 | Spring return damper actuator ( Nominal allowance of 2 per system for smoke control - TBC in detailed design), |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Spring return damper actuator | 200 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1088 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1089 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 30 |  |  | 0 | 0 | 0 | 0 | 0
1090 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1091 | [11 empty] | Item 14 | air pressure switch, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1092 | [8 empty] | Run and fault lights for Fire essential Chilled Water AHU with VSD |  |  | Item 15 | run light, |  |  | Run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1093 | [11 empty] | Item 16 | fault light, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1094 | [8 empty] | Auto/Off/On switch for Fire essential Chilled Water AHU with VSD |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1095 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1096 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface at MSSB for fire trade connection | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1097 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1098 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1099 | Shopping List | Fire essential Chilled Water AHU with VSD | MSSB |  |  |  |  | Electrical power supply and controls to Zero (0) Fire essential Chilled Water AHU with VSD. This includes supply and install of power and controls. Power for systems includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, 003 padlock, fan isolator and MSSB AS1668.1 trefolyte label. Controls for systems includes: Spring return damper actuator ( Nominal allowance of 2 per system for smoke control - TBC in detailed design), controls cabling, contactors/relays, air pressure switch, run light, fault light, Auto/Off/On switch, interface at MSSB for fire trade connection and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | Fire essential Chilled Water AHU with VSD | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1100 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1101 | [9 empty] | Zero | 0 | Fire essential Chilled Water AHU with VSD | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1102 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1103 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1104 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | FRC3025+E 2 hour fire for stair p | 4.83 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1105 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | Nill | 0 | 0 | VSD Car Park 3kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1106 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
1107 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1108 | [11 empty] | Item 7 | 003 padlock, |  |  |  | 0 | Nill | 0 | 0 | 003 Keyed Padlocks | 30 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1109 | [11 empty] | Item 8 | fan isolator and MSSB AS1668.1 trefolyte label. |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1110 | [11 empty] | Item 9 | Controls for systems includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1111 | [11 empty] | Item 10 | Spring return damper actuator ( Nominal allowance of 2 per system for smoke control - TBC in detailed design), |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Spring return damper actuator | 200 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1112 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1113 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 30 |  |  | 0 | 0 | 0 | 0 | 0
1114 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1115 | [11 empty] | Item 14 | air pressure switch, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1116 | [8 empty] | Run and fault lights for Fire essential Chilled Water AHU with VSD |  |  | Item 15 | run light, |  |  | Run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1117 | [11 empty] | Item 16 | fault light, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1118 | [8 empty] | Auto/Off/On switch for Fire essential Chilled Water AHU with VSD |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1119 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1120 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface at MSSB for fire trade connection | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1121 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1122 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1123 | Shopping List | Fire essential Chilled Water AHU with VSD | MSSB |  |  |  |  | Electrical power supply and controls to Zero (0) Fire essential Chilled Water AHU with VSD. This includes supply and install of power and controls. Power for systems includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, 003 padlock, fan isolator and MSSB AS1668.1 trefolyte label. Controls for systems includes: Spring return damper actuator ( Nominal allowance of 2 per system for smoke control - TBC in detailed design), controls cabling, contactors/relays, air pressure switch, run light, fault light, Auto/Off/On switch, interface at MSSB for fire trade connection and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | Fire essential Chilled Water AHU with VSD | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1124 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1125 | [9 empty] | Zero | 0 | Chilled Water Precision Cooling Unit | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1126 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 0 | per DOL Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1127 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1128 | [11 empty] | Item 3 | cabling to unit, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1129 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1130 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1131 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1132 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1133 | [11 empty] | Item 8 | fan isolator and trefolyte label. |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1134 | [11 empty] | Item 9 | Controls for systems includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1135 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1136 | [11 empty] | Item 11 | BMS terminals for flow fault indication, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1137 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 30 |  |  | 0 | 0 | 0 | 0 | 0
1138 | [11 empty] | Item 13 |  |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1139 | [11 empty] | Item 14 | air pressure switch , |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1140 | [8 empty] | Run and fault lights for Chilled Water Precision Cooling Unit |  |  | Item 15 | run light, |  |  | Run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1141 | [11 empty] | Item 16 | fault light, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1142 | [8 empty] | Auto/Off/On switch for Chilled Water Precision Cooling Unit |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1143 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1144 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1145 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1146 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1147 | Shopping List | Chilled Water Precision Cooling Unit | MSSB |  |  |  |  | Electrical power supply and controls to Zero (0) Chilled Water Precision Cooling Unit. This includes supply and install of power and controls. Power for systems includes: CB, cabling to unit, local isolator, fan isolator and trefolyte label. Controls for systems includes: BMS terminals for flow fault indication, controls cabling, air pressure switch , run light, fault light, Auto/Off/On switch, and commissioning/testing. | 0 |  | Price Check Summary: | Chilled Water Precision Cooling Unit | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1148 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1149 | [9 empty] | Zero | 0 | Chilled Water Fancoil Unit ( single speed) | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1150 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 0 | per DOL Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1151 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1152 | [11 empty] | Item 3 | cabling to unit, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1153 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1154 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1155 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1156 | [11 empty] | Item 7 | 003 padlock, |  |  |  | 0 | Nill | 0 | 0 | 003 Keyed Padlocks | 30 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1157 | [11 empty] | Item 8 | fan isolator and trefolyte label. |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1158 | [11 empty] | Item 9 | Controls for systems includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1159 | [11 empty] | Item 10 | BMS terminals for on/off control, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1160 | [11 empty] | Item 11 | BMS terminals for flow fault indication, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1161 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 30 |  |  | 0 | 0 | 0 | 0 | 0
1162 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1163 | [11 empty] | Item 14 | air pressure switch , |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1164 | [8 empty] | Run and fault lights for Chilled Water Fancoil Unit ( single speed) |  |  | Item 15 | run light, |  |  | Run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1165 | [11 empty] | Item 16 | fault light, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1166 | [8 empty] | Auto/Off/On switch for Chilled Water Fancoil Unit ( single speed) |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1167 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1168 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface at MSSB for fire trade connection | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1169 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1170 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1171 | Shopping List | Chilled Water Fancoil Unit ( single speed) | EITHER |  |  |  |  | Electrical power supply and controls to Zero (0) Chilled Water Fancoil Unit ( single speed). This includes supply and install of power and controls. Power for systems includes: CB, cabling to unit, local isolator, 003 padlock, fan isolator and trefolyte label. Controls for systems includes: BMS terminals for on/off control, BMS terminals for flow fault indication, controls cabling, contactors/relays, air pressure switch , run light, fault light, Auto/Off/On switch, interface at MSSB for fire trade connection and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | Chilled Water Fancoil Unit ( single speed) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1172 | Shopping List | [5 empty] | 19 | DX Air Conditioning |  | DX Air Conditioning | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0
1173 |  | Item |  |  |  |  | QTY | Inclusions Suggested Words | Cost | Exclusions Suggested Words | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1174 | [9 empty] | one | 1 | installation of VRF central controller | Electrical power supply and controls cabling for | By | Exclusions |  | 1 | Central Controller VRF | 1 | 4 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1175 | [11 empty] | Item 1 | circuit breaker, |  |  |  | 1 | Nill | 1 | 0 | CB 1 Phase 10A | 8.45 | 8.45 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1176 | [11 empty] | Item 2 | power supply from MSSB, |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | 2.5mm Twin and Earth | 0.85 | 17 | 20 | 1 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1177 | [11 empty] | Item 3 | interconnect controls cabling |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Network cable | 2 | 40 | 20 | 1 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1178 | [7 empty] | Coordination Note: - VRF supplier and commissioning team: Please refer to our exclusions relating to VRF central controller supply and commissioning. |  |  |  | Item 4 | and display install. | VRF supplier and commissioning team | VRF central controller supply and commissioning. |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1179 | [11 empty] | Item 5 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1180 | [11 empty] | Item 6 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1181 | [11 empty] | Item 7 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1182 | [11 empty] | Item 8 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1183 | [11 empty] | Item 9 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1184 | [11 empty] | Item 10 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1185 | [11 empty] | Item 11 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1186 | [11 empty] | Item 12 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0
1187 | [11 empty] | Item 13 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1188 | [11 empty] | Item 14 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1189 | [11 empty] | Item 15 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1190 | [11 empty] | Item 16 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1191 | [11 empty] | Item 17 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1192 | [11 empty] | Item 18 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1193 | [11 empty] | Item 19 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1194 | [11 empty] | Item 20 |  |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1195 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 385.45 |  |  |  | Total Labour Cost | 320 | 4 | Total Materials item 1 cost |  | 8.45 |  |  |  | Total continuous material cost |  | 57 |  |  |  | 385.45 |  | 0 | 0 | 0 | 0 | 0
1196 | Shopping List | installation of VRF central controller | EITHER |  |  |  | 1 | Electrical power supply and controls cabling for one (1) installation of VRF central controller. This includes supply and install of circuit breaker, power supply from MSSB, interconnect controls cabling and display install. Coordination Note: - VRF supplier and commissioning team: Please refer to our exclusions relating to VRF central controller supply and commissioning. | 385.45 | VRF central controller supply and commissioning. | Price Check Summary: | installation of VRF central controller | Average cost per system | 385.45 |  |  |  | Average hrs per system |  | 4 | Average cost per system |  | 8.45 |  |  |  | Average cost per system |  | 57 |  |  |  |  | 481.8125 | 385.45 | 320 | 8.45 | 57 | 0
1197 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1198 | [9 empty] | Zero | 0 | MSSB powered VRF outdoor units | Electrical power supply to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1199 | [11 empty] | Item 1 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 phase 50A (aprox size) | 36.2 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1200 | [11 empty] | Item 2 | cabling from MSSB to CU, |  |  |  | 0 | CU Unit - 10 to 20 m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1201 | [11 empty] | Item 3 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1202 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1203 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1204 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1205 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1206 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1207 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1208 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1209 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1210 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1211 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1212 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1213 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1214 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1215 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1216 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1217 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1218 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1219 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1220 | Shopping List | MSSB powered VRF outdoor units | MSSB |  |  |  |  | Electrical power supply to Zero (0) MSSB powered VRF outdoor units. This includes supply and install of CB, cabling from MSSB to CU, and local isolator. | 0 |  | Price Check Summary: | MSSB powered VRF outdoor units | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1221 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1222 | [9 empty] | four | 4 | VRF outdoor units | Electrical power supply to | By | Exclusions |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1223 | [7 empty] | Coordination Note: - Builder's Electrician : Please refer to our exclusions relating to local power supply and isolator for apartment condenser units. |  |  |  | Item 1 | cabling from electricians isolator to unit. | Builder's Electrician | local power supply and isolator for apartment condenser units. |  | 4 | CU Unit <1m cable | 4 | 2 | Nill | 0 | 0 | 4 | 4 | 1 | 4mm Cable 3 core and Earth | 2.9 | 11.6 | 4 | 4 | 1 |  |  | 0 | 0 | 0 | 0 | 0
1224 | [11 empty] | Item 2 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1225 | [11 empty] | Item 3 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1226 | [11 empty] | Item 4 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1227 | [11 empty] | Item 5 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1228 | [11 empty] | Item 6 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1229 | [11 empty] | Item 7 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1230 | [11 empty] | Item 8 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1231 | [11 empty] | Item 9 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1232 | [11 empty] | Item 10 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1233 | [11 empty] | Item 11 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1234 | [11 empty] | Item 12 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1235 | [11 empty] | Item 13 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1236 | [11 empty] | Item 14 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1237 | [11 empty] | Item 15 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1238 | [11 empty] | Item 16 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1239 | [11 empty] | Item 17 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1240 | [11 empty] | Item 18 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1241 | [11 empty] | Item 19 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1242 | [11 empty] | Item 20 |  |  |  |  | 4 | Nill | 4 | 0 | Nill | 0 | 0 | 4 | 4 | 1 | Nill | 0 | 0 | 0 | 4 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1243 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 171.6 |  |  |  | Total Labour Cost | 160 | 2 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 11.6 |  |  |  | 171.6 |  | 0 | 0 | 0 | 0 | 0
1244 | Shopping List | VRF outdoor units | LOCAL |  |  |  | 4 | Electrical power supply to four (4) VRF outdoor units. Each includes supply and install of cabling from electricians isolator to unit. Coordination Note: - Builder's Electrician : Please refer to our exclusions relating to local power supply and isolator for apartment condenser units. | 171.6 | local power supply and isolator for apartment condenser units. | Price Check Summary: | VRF outdoor units | Average cost per system | 42.9 |  |  |  | Average hrs per system |  | 0.5 | Average cost per system |  | 0 |  |  |  | Average cost per system |  | 2.9 |  |  |  |  | 214.5 | 171.6 | 160 | 0 | 11.6 | 0
1245 | [8 empty] | Extras |  | ` | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1246 | [9 empty] | Zero | 0 | split AC systems - MSSB powered with run and fault lights ( Excluding field wiring option) | Electrical power supply and controls cabling to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1247 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to interconnect cabling, |  |  |  | Item 1 |  | Customers in-house electrician | interconnect cabling, |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1248 | [11 empty] | Item 2 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1249 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to and local power isolator ( for Indoor unit). |  |  |  | Item 3 |  | Customers in-house electrician | and local power isolator ( for Indoor unit). |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1250 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to proprietary air-conditioning controllers supply and installation. |  |  |  | Item 4 |  | Customers in-house electrician | proprietary air-conditioning controllers supply and installation. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1251 | [11 empty] | Item 5 | circuit breaker, |  |  |  | 0 | Nill | 0 | 0 | CB 1 Phase 10A | 8.45 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1252 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Run signal controls cabling from each AC system adjacent to MSSB for run lights. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  |  |  | Item 6 | Run light and relay, | Customers in-house electrician | Run signal controls cabling from each AC system adjacent to MSSB for run lights. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1253 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Fault signal controls cabling from each AC system adjacent to MSSB for fault lights. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  |  |  | Item 7 | fault light and relay, | Customers in-house electrician | Fault signal controls cabling from each AC system adjacent to MSSB for fault lights. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1254 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to interface card for air-conditioning controllers for both run and fault indication. |  |  |  | Item 8 | connections of both controls and power cabling into MSSB, | AC system supplier | interface card for air-conditioning controllers for both run and fault indication. |  | 0 | Misc Install - 1hr | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1255 | [11 empty] | Item 9 | testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence), |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1256 | [11 empty] | Item 10 | Documented test results of final electrical systems and Form 16 certification. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1257 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1258 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Power cabling from MSSB to outdoor unit. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  |  |  | Item 12 |  | Customers in-house electrician | Power cabling from MSSB to outdoor unit. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1259 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1260 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1261 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1262 | [11 empty] | Item 16 |  | 0 |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1263 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1264 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1265 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1266 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1267 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1268 | Shopping List | split AC systems - MSSB powered with run and fault lights ( Excluding field wiring option) | MSSB | 4 | 6 | 10 |  | Electrical power supply and controls cabling to Zero (0) split AC systems - MSSB powered with run and fault lights ( Excluding field wiring option). This includes supply and install of circuit breaker, Run light and relay, fault light and relay, connections of both controls and power cabling into MSSB, testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence), Documented test results of final electrical systems and Form 16 certification. Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to interconnect cabling, Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to and local power isolator ( for Indoor unit). Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to proprietary air-conditioning controllers supply and installation. Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Run signal controls cabling from each AC system adjacent to MSSB for run lights. Customers electrician to leave tails adjacent MSSB for Controlworks to connect.Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Fault signal controls cabling from each AC system adjacent to MSSB for fault lights. Customers electrician to leave tails adjacent MSSB for Controlworks to connect.Coordination Note: - AC system supplier : Please refer to our exclusions relating to interface card for air-conditioning controllers for both run and fault indication. Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Power cabling from MSSB to outdoor unit. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. | 0 | interconnect cabling, and local power isolator ( for Indoor unit). proprietary air-conditioning controllers supply and installation. Run signal controls cabling from each AC system adjacent to MSSB for run lights. Customers electrician to leave tails adjacent MSSB for Controlworks to connect.Fault signal controls cabling from each AC system adjacent to MSSB for fault lights. Customers electrician to leave tails adjacent MSSB for Controlworks to connect.interface card for air-conditioning controllers for both run and fault indication. Power cabling from MSSB to outdoor unit. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. | Price Check Summary: | split AC systems - MSSB powered with run and fault lights ( Excluding field wiring option) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1269 | [8 empty] | Extras |  | ` | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1270 | [9 empty] | Zero | 0 | split AC systems - MSSB powered with run lights ( Excluding field wiring option) | Electrical power supply and controls cabling to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1271 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to interconnect cabling, |  |  |  | Item 1 |  | Customers in-house electrician | interconnect cabling, |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1272 | [11 empty] | Item 2 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1273 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to and local power isolator ( for Indoor unit). |  |  |  | Item 3 |  | Customers in-house electrician | and local power isolator ( for Indoor unit). |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1274 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to proprietary air-conditioning controllers supply and installation. |  |  |  | Item 4 |  | Customers in-house electrician | proprietary air-conditioning controllers supply and installation. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1275 | [11 empty] | Item 5 | circuit breaker, |  |  |  | 0 | Nill | 0 | 0 | CB 1 Phase 10A | 8.45 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1276 | [11 empty] | Item 6 | Run light and current switch, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1277 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1278 | [11 empty] | Item 8 | connections of power cabling into MSSB, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1279 | [11 empty] | Item 9 | testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence), |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1280 | [11 empty] | Item 10 | Documented test results of final electrical systems and Form 16 certification. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1281 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1282 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Power cabling from MSSB to outdoor unit. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  |  |  | Item 12 |  | Customers in-house electrician | Power cabling from MSSB to outdoor unit. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1283 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1284 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1285 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1286 | [11 empty] | Item 16 |  | 0 |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1287 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1288 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1289 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1290 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1291 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1292 | Shopping List | split AC systems - MSSB powered with run lights ( Excluding field wiring option) | MSSB | 4 | 6 |  |  | Electrical power supply and controls cabling to Zero (0) split AC systems - MSSB powered with run lights ( Excluding field wiring option). This includes supply and install of circuit breaker, Run light and current switch, connections of power cabling into MSSB, testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence), Documented test results of final electrical systems and Form 16 certification. Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to interconnect cabling, Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to and local power isolator ( for Indoor unit). Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to proprietary air-conditioning controllers supply and installation. Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Power cabling from MSSB to outdoor unit. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. | 0 | interconnect cabling, and local power isolator ( for Indoor unit). proprietary air-conditioning controllers supply and installation. Power cabling from MSSB to outdoor unit. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. | Price Check Summary: | split AC systems - MSSB powered with run lights ( Excluding field wiring option) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1293 | [8 empty] | Extras |  | ` | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1294 | [9 empty] | Zero | 0 | DX CRAC Systems - MSSB powered with run and fault lights | Electrical power supply and controls cabling to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1295 | [11 empty] | Item 1 | interconnect cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1296 | [11 empty] | Item 2 | power cabling from outdoor unit |  |  |  | 0 | Cond Unit Sml Dx | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1297 | [11 empty] | Item 3 | and local power isolator ( for Indoor unit). |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1298 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to proprietary air-conditioning controllers. |  |  |  | Item 4 | Each system includes install only of proprietary controller. | AC system supplier | proprietary air-conditioning controllers. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1299 | [11 empty] | Item 5 | CB and Power cabling from MSSB to outdoor unit. |  |  |  | 0 | Cabling 10-20m | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1300 | [11 empty] | Item 6 | Run light, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1301 | [11 empty] | Item 7 | fault light, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1302 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to interface card for air-conditioning controllers. |  |  |  | Item 8 | controls cabling between MSSB and outdoor unit ( for run and fault lights), | AC system supplier | interface card for air-conditioning controllers. |  | 0 | Misc Install - 1hr | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1303 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1304 | [11 empty] | Item 10 |  |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1305 | [11 empty] | Item 11 |  |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1306 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1307 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1308 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1309 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1310 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1311 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1312 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1313 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1314 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1315 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1316 | Shopping List | DX CRAC Systems - MSSB powered with run and fault lights | MSSB | 4 | 6 | 10 |  | Electrical power supply and controls cabling to Zero (0) DX CRAC Systems - MSSB powered with run and fault lights. This includes supply and install of interconnect cabling, power cabling from outdoor unit and local power isolator ( for Indoor unit). Each system includes install only of proprietary controller. CB and Power cabling from MSSB to outdoor unit. Run light, fault light, controls cabling between MSSB and outdoor unit ( for run and fault lights), Coordination Note: - AC system supplier : Please refer to our exclusions relating to proprietary air-conditioning controllers. Coordination Note: - AC system supplier : Please refer to our exclusions relating to interface card for air-conditioning controllers. | 0 | proprietary air-conditioning controllers. interface card for air-conditioning controllers. | Price Check Summary: | DX CRAC Systems - MSSB powered with run and fault lights | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1317 | [8 empty] | Extras |  | ` | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1318 | [9 empty] | Zero | 0 | split AC systems - MSSB powered with run and fault lights | Electrical power supply and controls cabling to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1319 | [11 empty] | Item 1 | interconnect cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1320 | [11 empty] | Item 2 | power cabling from outdoor unit |  |  |  | 0 | Cond Unit Sml Dx | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1321 | [11 empty] | Item 3 | and local power isolator ( for Indoor unit). |  |  |  | 0 | Nill | 0 | 0 | 1 phase isolator WP135 | 19.8 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1322 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to proprietary air-conditioning controllers. |  |  |  | Item 4 | Each system includes install only of proprietary controller. | AC system supplier | proprietary air-conditioning controllers. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1323 | [11 empty] | Item 5 | CB and Power cabling from MSSB to outdoor unit. |  |  |  | 0 | Cabling 10-20m | 0 | 0 | CB 1 Phase 10A | 8.45 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1324 | [11 empty] | Item 6 | Run light, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1325 | [11 empty] | Item 7 | fault light, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1326 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to interface card for air-conditioning controllers. |  |  |  | Item 8 | controls cabling between MSSB and outdoor unit ( for run and fault lights), | AC system supplier | interface card for air-conditioning controllers. |  | 0 | Misc Install - 1hr | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1327 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1328 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1329 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1330 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1331 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1332 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1333 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1334 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1335 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1336 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1337 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1338 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1339 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1340 | Shopping List | split AC systems - MSSB powered with run and fault lights | MSSB | 4 | 6 | 10 |  | Electrical power supply and controls cabling to Zero (0) split AC systems - MSSB powered with run and fault lights. This includes supply and install of interconnect cabling, power cabling from outdoor unit and local power isolator ( for Indoor unit). Each system includes install only of proprietary controller. CB and Power cabling from MSSB to outdoor unit. Run light, fault light, controls cabling between MSSB and outdoor unit ( for run and fault lights), Coordination Note: - AC system supplier : Please refer to our exclusions relating to proprietary air-conditioning controllers. Coordination Note: - AC system supplier : Please refer to our exclusions relating to interface card for air-conditioning controllers. | 0 | proprietary air-conditioning controllers. interface card for air-conditioning controllers. | Price Check Summary: | split AC systems - MSSB powered with run and fault lights | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1341 | [8 empty] | Extras |  | ` | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1342 | [9 empty] | Zero | 0 | Multihead split AC systems (local power supply) - 4 indoor units with wireless controlers | Electrical power supply and controls cabling to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1343 | [11 empty] | Item 1 | interconnect cabling, |  |  |  | 0 | Misc Install - 2.5hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1344 | [11 empty] | Item 2 | power cabling from outdoor unit |  |  |  | 0 | CU Unit <1m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1345 | [11 empty] | Item 3 | and local power isolator ( for Indoor unit). |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1346 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to wireless air-conditioning controllers. |  |  |  | Item 4 |  | AC system supplier | wireless air-conditioning controllers. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1347 | [7 empty] | Coordination Note: - Builders Electrician: Please refer to our exclusions relating to power supply to outdoor unit |  |  |  | Item 5 | Power cabling from electricians isolator to outdoor unit. | Builders Electrician | power supply to outdoor unit |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1348 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1349 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1350 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1351 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1352 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1353 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1354 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1355 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1356 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1357 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1358 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1359 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1360 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1361 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1362 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1363 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1364 | Shopping List | Multihead split AC systems (local power supply) - 4 indoor units with wireless controlers | LOCAL | 4 | 6 | 10 |  | Electrical power supply and controls cabling to Zero (0) Multihead split AC systems (local power supply) - 4 indoor units with wireless controlers. This includes supply and install of interconnect cabling, power cabling from outdoor unit and local power isolator ( for Indoor unit). Power cabling from electricians isolator to outdoor unit. Coordination Note: - AC system supplier : Please refer to our exclusions relating to wireless air-conditioning controllers. Coordination Note: - Builders Electrician: Please refer to our exclusions relating to power supply to outdoor unit | 0 | wireless air-conditioning controllers. power supply to outdoor unit | Price Check Summary: | Multihead split AC systems (local power supply) - 4 indoor units with wireless controlers | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1365 | [8 empty] | Extras |  | ` | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1366 | [9 empty] | Zero | 0 | Multihead split AC systems (local power supply) - 3 indoor units with wireless controlers | Electrical power supply and controls cabling to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1367 | [11 empty] | Item 1 | interconnect cabling, |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1368 | [11 empty] | Item 2 | power cabling from outdoor unit |  |  |  | 0 | CU Unit <1m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1369 | [11 empty] | Item 3 | and local power isolator ( for Indoor unit). |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1370 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to wireless air-conditioning controllers. |  |  |  | Item 4 |  | AC system supplier | wireless air-conditioning controllers. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1371 | [7 empty] | Coordination Note: - Builders Electrician: Please refer to our exclusions relating to power supply to outdoor unit |  |  |  | Item 5 | Power cabling from electricians isolator to outdoor unit. | Builders Electrician | power supply to outdoor unit |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1372 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1373 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1374 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1375 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1376 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1377 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1378 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1379 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1380 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1381 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1382 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1383 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1384 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1385 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1386 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1387 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1388 | Shopping List | Multihead split AC systems (local power supply) - 3 indoor units with wireless controlers | LOCAL | 4 | 6 | 10 |  | Electrical power supply and controls cabling to Zero (0) Multihead split AC systems (local power supply) - 3 indoor units with wireless controlers. This includes supply and install of interconnect cabling, power cabling from outdoor unit and local power isolator ( for Indoor unit). Power cabling from electricians isolator to outdoor unit. Coordination Note: - AC system supplier : Please refer to our exclusions relating to wireless air-conditioning controllers. Coordination Note: - Builders Electrician: Please refer to our exclusions relating to power supply to outdoor unit | 0 | wireless air-conditioning controllers. power supply to outdoor unit | Price Check Summary: | Multihead split AC systems (local power supply) - 3 indoor units with wireless controlers | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1389 | [8 empty] | Extras |  | ` | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1390 | [9 empty] | Zero | 0 | Multihead split AC systems (local power supply) - 2 indoor units with wireless controlers | Electrical power supply and controls cabling to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1391 | [11 empty] | Item 1 | interconnect cabling, |  |  |  | 0 | Misc Install - 1.5hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1392 | [11 empty] | Item 2 | power cabling from outdoor unit |  |  |  | 0 | CU Unit <1m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1393 | [11 empty] | Item 3 | and local power isolator ( for Indoor unit). |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1394 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to wireless air-conditioning controllers. |  |  |  | Item 4 |  | AC system supplier | wireless air-conditioning controllers. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1395 | [7 empty] | Coordination Note: - Builders Electrician: Please refer to our exclusions relating to power supply to outdoor unit |  |  |  | Item 5 | Power cabling from electricians isolator to outdoor unit. | Builders Electrician | power supply to outdoor unit |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1396 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1397 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1398 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1399 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1400 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1401 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1402 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1403 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1404 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1405 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1406 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1407 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1408 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1409 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1410 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1411 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1412 | Shopping List | Multihead split AC systems (local power supply) - 2 indoor units with wireless controlers | LOCAL | 4 | 6 | 10 |  | Electrical power supply and controls cabling to Zero (0) Multihead split AC systems (local power supply) - 2 indoor units with wireless controlers. This includes supply and install of interconnect cabling, power cabling from outdoor unit and local power isolator ( for Indoor unit). Power cabling from electricians isolator to outdoor unit. Coordination Note: - AC system supplier : Please refer to our exclusions relating to wireless air-conditioning controllers. Coordination Note: - Builders Electrician: Please refer to our exclusions relating to power supply to outdoor unit | 0 | wireless air-conditioning controllers. power supply to outdoor unit | Price Check Summary: | Multihead split AC systems (local power supply) - 2 indoor units with wireless controlers | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1413 | [8 empty] | Extras |  | ` | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1414 | [9 empty] | Zero | 0 | split AC systems (local power supply) | Electrical power supply and controls cabling to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1415 | [11 empty] | Item 1 | interconnect cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1416 | [11 empty] | Item 2 | power cabling from outdoor unit |  |  |  | 0 | Cond Unit Sml Dx | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1417 | [11 empty] | Item 3 | and local power isolator ( for Indoor unit). |  |  |  | 0 | Nill | 0 | 0 | 1 phase isolator WP135 | 19.8 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1418 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to proprietary air-conditioning controllers. |  |  |  | Item 4 | Each system includes install only of proprietary controller. | AC system supplier | proprietary air-conditioning controllers. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1419 | [11 empty] | Item 5 | CB and Power cabling from electricians isolator to outdoor unit. |  |  |  | 0 | Cabling 10-20m | 0 | 0 | CB 1 Phase 10A | 8.45 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1420 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1421 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1422 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1423 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1424 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1425 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1426 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1427 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1428 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1429 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1430 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1431 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1432 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1433 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1434 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1435 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1436 | Shopping List | split AC systems (local power supply) | LOCAL | 4 | 6 | 10 |  | Electrical power supply and controls cabling to Zero (0) split AC systems (local power supply). This includes supply and install of interconnect cabling, power cabling from outdoor unit and local power isolator ( for Indoor unit). Each system includes install only of proprietary controller. CB and Power cabling from electricians isolator to outdoor unit. Coordination Note: - AC system supplier : Please refer to our exclusions relating to proprietary air-conditioning controllers. | 0 | proprietary air-conditioning controllers. | Price Check Summary: | split AC systems (local power supply) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1437 | [8 empty] | Extras |  | ` | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1438 | [9 empty] | Zero | 0 | common area split AC systems (local power supply) | Electrical power supply and controls cabling to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1439 | [11 empty] | Item 1 | interconnect cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1440 | [11 empty] | Item 2 | power cabling from outdoor unit |  |  |  | 0 | Cond Unit Sml Dx | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1441 | [11 empty] | Item 3 | and local power isolator ( for Indoor unit). |  |  |  | 0 | Nill | 0 | 0 | 1 phase isolator WP135 | 19.8 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1442 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to proprietary air-conditioning controllers. |  |  |  | Item 4 | Each system includes install only of proprietary controller. | AC system supplier | proprietary air-conditioning controllers. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1443 | [7 empty] | Coordination Note: - Builders Electrician : Please refer to our exclusions relating to local power supply and isolator for common area split AC systems condenser units. |  |  |  | Item 5 | Power cabling from electricians isolator to outdoor unit. | Builders Electrician | local power supply and isolator for common area split AC systems condenser units. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1444 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1445 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1446 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1447 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1448 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1449 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1450 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1451 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1452 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1453 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1454 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1455 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1456 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1457 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1458 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1459 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1460 | Shopping List | common area split AC systems (local power supply) | LOCAL | 4 | 6 | 10 |  | Electrical power supply and controls cabling to Zero (0) common area split AC systems (local power supply). This includes supply and install of interconnect cabling, power cabling from outdoor unit and local power isolator ( for Indoor unit). Each system includes install only of proprietary controller. Power cabling from electricians isolator to outdoor unit. Coordination Note: - AC system supplier : Please refer to our exclusions relating to proprietary air-conditioning controllers. Coordination Note: - Builders Electrician : Please refer to our exclusions relating to local power supply and isolator for common area split AC systems condenser units. | 0 | proprietary air-conditioning controllers. local power supply and isolator for common area split AC systems condenser units. | Price Check Summary: | common area split AC systems (local power supply) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1461 | [8 empty] | Extras |  | ` | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1462 | [9 empty] | Zero | 0 | VRF indoor units with cabling for on/off control from other system/s to unit | Electrical power supply and controls cabling to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1463 | [11 empty] | Item 1 | interconnect cabling, |  |  |  | 0 | VRF Network | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1464 | [11 empty] | Item 2 | CB, power cabling from outdoor unit |  |  |  | 0 | Ducted VRF Unit < 10m | 0 | 0 | CB 1 Phase 10A | 8.45 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1465 | [11 empty] | Item 3 | and local power isolator. |  |  |  | 0 | Nill | 0 | 0 | 1 phase isolator WP135 | 19.8 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1466 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to proprietary air-conditioning controllers. |  |  |  | Item 4 | Each system includes install only of proprietary controller. | AC system supplier | proprietary air-conditioning controllers. |  | 0 | Wall Controller VRF | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1467 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to AC interface card with on/off control contactors. |  |  |  | Item 5 | Each system includes cabling from units for interlock with other system. | AC system supplier | AC interface card with on/off control contactors. |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 15 |  |  | 0 | 0 | 0 | 0 | 0
1468 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1469 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1470 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1471 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1472 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1473 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1474 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1475 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1476 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1477 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1478 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1479 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1480 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1481 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1482 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1483 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1484 | Shopping List | VRF indoor units with cabling for on/off control from other system/s to unit | MSSB |  |  |  |  | Electrical power supply and controls cabling to Zero (0) VRF indoor units with cabling for on/off control from other system/s to unit. This includes supply and install of interconnect cabling, CB, power cabling from outdoor unit and local power isolator. Each system includes install only of proprietary controller. Each system includes cabling from units for interlock with other system. Coordination Note: - AC system supplier : Please refer to our exclusions relating to proprietary air-conditioning controllers.Coordination Note: - AC system supplier : Please refer to our exclusions relating to AC interface card with on/off control contactors. | 0 | proprietary air-conditioning controllers.AC interface card with on/off control contactors. | Price Check Summary: | VRF indoor units with cabling for on/off control from other system/s to unit | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1485 | [8 empty] | Extras |  | ` | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1486 | [9 empty] | Zero | 0 | VRF indoor units with cabling for run status from unit to other system/s | Electrical power supply and controls cabling to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1487 | [11 empty] | Item 1 | interconnect cabling, |  |  |  | 0 | VRF Network | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1488 | [11 empty] | Item 2 | CB, power cabling from outdoor unit |  |  |  | 0 | Ducted VRF Unit < 10m | 0 | 0 | CB 1 Phase 10A | 8.45 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1489 | [11 empty] | Item 3 | and local power isolator. |  |  |  | 0 | Nill | 0 | 0 | 1 phase isolator WP135 | 19.8 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1490 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to proprietary air-conditioning controllers. |  |  |  | Item 4 | Each system includes install only of proprietary controller. | AC system supplier | proprietary air-conditioning controllers. |  | 0 | Wall Controller VRF | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1491 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to AC interface card with system status contactors. |  |  |  | Item 5 | Each system includes cabling from units for interlock with other system. | AC system supplier | AC interface card with system status contactors. |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 15 |  |  | 0 | 0 | 0 | 0 | 0
1492 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1493 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1494 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1495 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1496 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1497 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1498 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1499 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1500 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1501 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1502 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1503 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1504 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1505 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1506 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1507 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1508 | Shopping List | VRF indoor units with cabling for run status from unit to other system/s | MSSB |  |  |  |  | Electrical power supply and controls cabling to Zero (0) VRF indoor units with cabling for run status from unit to other system/s. This includes supply and install of interconnect cabling, CB, power cabling from outdoor unit and local power isolator. Each system includes install only of proprietary controller. Each system includes cabling from units for interlock with other system. Coordination Note: - AC system supplier : Please refer to our exclusions relating to proprietary air-conditioning controllers.Coordination Note: - AC system supplier : Please refer to our exclusions relating to AC interface card with system status contactors. | 0 | proprietary air-conditioning controllers.AC interface card with system status contactors. | Price Check Summary: | VRF indoor units with cabling for run status from unit to other system/s | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1509 | [8 empty] | Extras |  | ` | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1510 | [9 empty] | fourteen | 14 | VRF indoor units | Electrical power supply and controls cabling to | By | Exclusions |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1511 | [11 empty] | Item 1 | controls cabling, |  |  |  | 14 | VRF Network | 14 | 3.5 | Nill | 0 | 0 | 14 | 14 | 1 | 7030 2 pair TCAS7302P | 0.88 | 123.2 | 140 | 14 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1512 | [11 empty] | Item 2 | CB, power cabling from outdoor unit |  |  |  | 14 | Ducted VRF Unit < 10m | 14 | 35 | CB 1 Phase 10A | 8.45 | 118.3 | 14 | 14 | 1 | 2.5mm Twin and Earth | 0.85 | 119 | 140 | 14 | 10 |  |  | 0 | 0 | 0 | 0 | 0
1513 | [11 empty] | Item 3 | and local power isolator. |  |  |  | 14 | Nill | 14 | 0 | 1 phase isolator WP135 | 19.8 | 277.2 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1514 | [7 empty] | Coordination Note: - AC system supplier : Please refer to our exclusions relating to proprietary air-conditioning controllers. |  |  |  | Item 4 | Each system includes install only of proprietary controller. | AC system supplier | proprietary air-conditioning controllers. |  | 14 | Wall Controller VRF | 14 | 7 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1515 | [11 empty] | Item 5 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1516 | [11 empty] | Item 6 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1517 | [11 empty] | Item 7 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1518 | [11 empty] | Item 8 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1519 | [11 empty] | Item 9 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1520 | [11 empty] | Item 10 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1521 | [11 empty] | Item 11 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1522 | [11 empty] | Item 12 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1523 | [11 empty] | Item 13 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1524 | [11 empty] | Item 14 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1525 | [11 empty] | Item 15 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1526 | [11 empty] | Item 16 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1527 | [11 empty] | Item 17 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1528 | [11 empty] | Item 18 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1529 | [11 empty] | Item 19 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1530 | [11 empty] | Item 20 |  |  |  |  | 14 | Nill | 14 | 0 | Nill | 0 | 0 | 14 | 14 | 1 | Nill | 0 | 0 | 0 | 14 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1531 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 4277.7 |  |  |  | Total Labour Cost | 3640 | 45.5 | Total Materials item 1 cost |  | 395.5 |  |  |  | Total continuous material cost |  | 242.2 |  |  |  | 4277.7 |  | 0 | 0 | 0 | 0 | 0
1532 | Shopping List | VRF indoor units | EITHER |  |  |  | 14 | Electrical power supply and controls cabling to fourteen (14) VRF indoor units. Each includes supply and install of controls cabling, CB, power cabling from outdoor unit and local power isolator. Each system includes install only of proprietary controller. Coordination Note: - AC system supplier : Please refer to our exclusions relating to proprietary air-conditioning controllers. | 4277.7 | proprietary air-conditioning controllers. | Price Check Summary: | VRF indoor units | Average cost per system | 305.55 |  |  |  | Average hrs per system |  | 3.25 | Average cost per system |  | 28.25 |  |  |  | Average cost per system |  | 17.3 |  |  |  |  | 5347.125 | 4277.7 | 3640 | 395.5 | 242.2 | 0
1533 | [8 empty] | Extras |  | ` | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1534 | [9 empty] | Zero | 0 | Ducted VRF indoor fan coil units | Electrical power supply and controls cabling to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1535 | [11 empty] | Item 1 | controls cabling, |  |  |  | 0 | VRF Network | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 30 |  |  | 0 | 0 | 0 | 0 | 0
1536 | [11 empty] | Item 2 | CB, power cabling from outdoor unit |  |  |  | 0 | Ducted VRF Unit 10-30m cable | 0 | 0 | CB 1 Phase 10A | 8.45 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 30 |  |  | 0 | 0 | 0 | 0 | 0
1537 | [11 empty] | Item 3 | and local power isolator. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1538 | [7 empty] | Coordination Note: - AC system supplier: Please refer to our exclusions relating to proprietary air-conditioning controllers. |  |  |  | Item 4 | Each system includes install only of proprietary controller | AC system supplier | proprietary air-conditioning controllers. |  | 0 | Wall Controller VRF | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1539 | [7 empty] | Coordination Note: - AC system supplier: Please refer to our exclusions relating to proprietary air-conditioning interconnect cabling for branch connector boxes. |  |  |  | Item 5 | and install only of branch connector boxes interconnect cabling. | AC system supplier | proprietary air-conditioning interconnect cabling for branch connector boxes. |  | 0 | Branch Box for Heat Recovery | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1540 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1541 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1542 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1543 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1544 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1545 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1546 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1547 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1548 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1549 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1550 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1551 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1552 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1553 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1554 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1555 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1556 | Shopping List | Ducted VRF indoor fan coil units | EITHER |  |  |  |  | Electrical power supply and controls cabling to Zero (0) Ducted VRF indoor fan coil units. This includes supply and install of controls cabling, CB, power cabling from outdoor unit and local power isolator. Each system includes install only of proprietary controller and install only of branch connector boxes interconnect cabling. Coordination Note: - AC system supplier: Please refer to our exclusions relating to proprietary air-conditioning controllers. Coordination Note: - AC system supplier: Please refer to our exclusions relating to proprietary air-conditioning interconnect cabling for branch connector boxes. | 0 | proprietary air-conditioning controllers. proprietary air-conditioning interconnect cabling for branch connector boxes. | Price Check Summary: | Ducted VRF indoor fan coil units | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1557 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
1558 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
1559 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1560 | [9 empty] | Zero | 0 | Packaged units | Electrical power supply to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1561 | [11 empty] | Item 1 | CB, cabling from MSSB |  |  |  | 0 | CU Unit - 10 to 20 m cable | 0 | 0 | CB 3 phase 50A (aprox size) | 36.2 | 0 | 0 | 0 | 1 | 6mm Cable 3 core and Earth | 3.8 | 0 | 0 | 0 | 15 |  |  | 0 | 0 | 0 | 0 | 0
1562 | [11 empty] | Item 2 |  |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1563 | [11 empty] | Item 3 |  |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1564 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1565 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1566 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1567 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1568 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1569 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1570 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1571 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1572 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1573 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1574 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1575 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1576 | [11 empty] | Item 16 |  | 0 |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1577 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1578 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1579 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1580 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1581 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1582 | Shopping List | Packaged units | MSSB |  | 2 |  |  | Electrical power supply to Zero (0) Packaged units. This includes supply and install of CB, cabling from MSSB | 0 |  | Price Check Summary: | Packaged units | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1583 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1584 | [9 empty] | Zero | 0 | Packaged units (Field wiring by customer) | Electrical power supply to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1585 | [11 empty] | Item 1 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 phase 50A (aprox size) | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 15 |  |  | 0 | 0 | 0 | 0 | 0
1586 | [11 empty] | Item 2 | Run light and Fault light, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1587 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to power cabling from MSSB and local power isolator ( for PAC unit). |  |  |  | Item 3 |  | Customers in-house electrician | power cabling from MSSB and local power isolator ( for PAC unit). |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1588 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to proprietary air-conditioning controllers supply and installation. |  |  |  | Item 4 | connections of power cabling into MSSB, | Customers in-house electrician | proprietary air-conditioning controllers supply and installation. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1589 | [11 empty] | Item 5 | testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence), |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1590 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to run and fault cabling from PAC unit to MSSB |  |  |  | Item 6 | Documented test results of final electrical systems and Form 16 certification. | Customers in-house electrician | run and fault cabling from PAC unit to MSSB |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1591 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1592 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1593 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1594 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1595 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1596 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Power cabling from MSSB to PAC unit. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  |  |  | Item 12 |  | Customers in-house electrician | Power cabling from MSSB to PAC unit. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1597 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1598 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1599 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1600 | [11 empty] | Item 16 |  | 0 |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1601 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1602 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1603 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1604 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1605 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1606 | Shopping List | Packaged units (Field wiring by customer) | MSSB |  | 2 |  |  | Electrical power supply to Zero (0) Packaged units (Field wiring by customer). This includes supply and install of CB, Run light and Fault light, connections of power cabling into MSSB, testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence), Documented test results of final electrical systems and Form 16 certification. Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to power cabling from MSSB and local power isolator ( for PAC unit). Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to proprietary air-conditioning controllers supply and installation. Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to run and fault cabling from PAC unit to MSSB Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Power cabling from MSSB to PAC unit. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. | 0 | power cabling from MSSB and local power isolator ( for PAC unit). proprietary air-conditioning controllers supply and installation. run and fault cabling from PAC unit to MSSB Power cabling from MSSB to PAC unit. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. | Price Check Summary: | Packaged units (Field wiring by customer) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1607 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1608 | [9 empty] | Zero | 0 | Office VRF outdoor units | Electrical power supply to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1609 | [11 empty] | Item 1 | CB, cabling from MSSB |  |  |  | 0 | CU Unit - 10 to 20 m cable | 0 | 0 | CB 3 phase 50A (aprox size) | 36.2 | 0 | 0 | 0 | 1 | 6mm Cable 3 core and Earth | 3.8 | 0 | 0 | 0 | 15 |  |  | 0 | 0 | 0 | 0 | 0
1610 | [11 empty] | Item 2 | and local isolator. |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1611 | [11 empty] | Item 3 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1612 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1613 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1614 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1615 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1616 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1617 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1618 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1619 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1620 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1621 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1622 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1623 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1624 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1625 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1626 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1627 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1628 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1629 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1630 | Shopping List | Office VRF outdoor units | MSSB |  |  |  |  | Electrical power supply to Zero (0) Office VRF outdoor units. This includes supply and install of CB, cabling from MSSB and local isolator. | 0 |  | Price Check Summary: | Office VRF outdoor units | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1631 | Shopping List | [5 empty] | 0 | Chilled Water |  | Chilled Water | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0
1632 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1633 | [9 empty] | Zero | 0 | Small Coolingwater Aircooled Chillers - from Chiller MSSB | Electrical power supply to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1634 | [11 empty] | Item 1 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1635 | [11 empty] | Item 2 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1636 | [11 empty] | Item 3 | Cabling to chiller, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1637 | [11 empty] | Item 4 | cable ladder with mechanical protection, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1638 | [11 empty] | Item 5 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1639 | [11 empty] | Item 6 | and commissioning/testing. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1640 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1641 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1642 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1643 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1644 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1645 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1646 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1647 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1648 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1649 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1650 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1651 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1652 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1653 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1654 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1655 | Shopping List | Small Coolingwater Aircooled Chillers - from Chiller MSSB | MSSB |  |  | 2 |  | Electrical power supply to Zero (0) Small Coolingwater Aircooled Chillers - from Chiller MSSB. This includes supply and install of Cabling to chiller, cable ladder with mechanical protection, trefolyte labelling, and commissioning/testing. | 0 |  | Price Check Summary: | Small Coolingwater Aircooled Chillers - from Chiller MSSB | Average cost per system | 1000 |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1656 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1657 | [9 empty] | Zero | 0 | Small Aircooled Chillers - from Chiller MSSB | Electrical power supply to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1658 | [11 empty] | Item 1 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1659 | [11 empty] | Item 2 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1660 | [11 empty] | Item 3 | Cabling to chiller, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1661 | [11 empty] | Item 4 | cable ladder with mechanical protection, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1662 | [11 empty] | Item 5 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1663 | [11 empty] | Item 6 | and commissioning/testing. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1664 | [11 empty] | Item 7 | Please Note: Chiller MSSB is a specialist custom made system including required components for chiller power supply. Details to be determined following consultants detailed design. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1665 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1666 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1667 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1668 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1669 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1670 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1671 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1672 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1673 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1674 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1675 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1676 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1677 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1678 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1679 | Shopping List | Small Aircooled Chillers - from Chiller MSSB | MSSB |  |  | 2 |  | Electrical power supply to Zero (0) Small Aircooled Chillers - from Chiller MSSB. This includes supply and install of Cabling to chiller, cable ladder with mechanical protection, trefolyte labelling, and commissioning/testing. Please Note: Chiller MSSB is a specialist custom made system including required components for chiller power supply. Details to be determined following consultants detailed design. | 0 |  | Price Check Summary: | Small Aircooled Chillers - from Chiller MSSB | Average cost per system | 2000 |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1680 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1681 | [9 empty] | Zero | 0 | Medium Aircooled Chillers - from Chiller MSSB | Electrical power supply to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1682 | [11 empty] | Item 1 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1683 | [11 empty] | Item 2 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1684 | [11 empty] | Item 3 | Cabling to chiller, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1685 | [11 empty] | Item 4 | cable ladder with mechanical protection, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1686 | [11 empty] | Item 5 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1687 | [11 empty] | Item 6 | and commissioning/testing. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1688 | [11 empty] | Item 7 | Please Note: Chiller MSSB is a specialist custom made system including required components for chiller power supply. Details to be determined following consultants detailed design. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1689 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1690 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1691 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1692 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1693 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1694 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1695 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1696 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1697 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1698 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1699 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1700 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1701 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1702 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1703 | Shopping List | Medium Aircooled Chillers - from Chiller MSSB | MSSB |  |  |  |  | Electrical power supply to Zero (0) Medium Aircooled Chillers - from Chiller MSSB. This includes supply and install of Cabling to chiller, cable ladder with mechanical protection, trefolyte labelling, and commissioning/testing. Please Note: Chiller MSSB is a specialist custom made system including required components for chiller power supply. Details to be determined following consultants detailed design. | 0 |  | Price Check Summary: | Medium Aircooled Chillers - from Chiller MSSB | Average cost per system | 2500 |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1704 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1705 | [9 empty] | Zero | 0 | Small VSD pump - from MSSB power supply and BMS interface provisions | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1706 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1707 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1708 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1709 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | per VSD Fan | 0 | 0 | VSD 5.5kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1710 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
1711 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1712 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1713 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1714 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1715 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1716 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1717 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
1718 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1719 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1720 | [8 empty] | run and fault lights for Small VSD pump - from MSSB power supply and BMS interface provisions |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1721 | [11 empty] | Item 16 | current switch for pump status, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1722 | [8 empty] | Auto/Off/On switch for Small VSD pump - from MSSB power supply and BMS interface provisions |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1723 | [11 empty] | Item 18 | BMS terminals for on/off control, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1724 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1725 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1726 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1727 | Shopping List | Small VSD pump - from MSSB power supply and BMS interface provisions | MSSB |  |  |  |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) Small VSD pump - from MSSB power supply and BMS interface provisions. This includes supply and install of power and controls. Power for system includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, Controls for system includes: controls cabling, contactors/relays, run and fault lights, current switch for pump status, Auto/Off/On switch, BMS terminals for on/off control, trefolyte labelling, and commissioning/testing. | 0 |  | Price Check Summary: | Small VSD pump - from MSSB power supply and BMS interface provisions | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1728 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1729 | [9 empty] | Zero | 0 | Small DOL pump - from MSSB power supply and BMS interface provisions | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1730 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1731 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1732 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1733 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | per DOL Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1734 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
1735 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1736 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1737 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1738 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1739 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1740 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1741 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
1742 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1743 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1744 | [8 empty] | run and fault lights for Small DOL pump - from MSSB power supply and BMS interface provisions |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1745 | [11 empty] | Item 16 | current switch for pump status, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1746 | [8 empty] | Auto/Off/On switch for Small DOL pump - from MSSB power supply and BMS interface provisions |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1747 | [11 empty] | Item 18 | BMS terminals for on/off control, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1748 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1749 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1750 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1751 | Shopping List | Small DOL pump - from MSSB power supply and BMS interface provisions | MSSB |  |  |  |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) Small DOL pump - from MSSB power supply and BMS interface provisions. This includes supply and install of power and controls. Power for system includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, Controls for system includes: controls cabling, contactors/relays, run and fault lights, current switch for pump status, Auto/Off/On switch, BMS terminals for on/off control, trefolyte labelling, and commissioning/testing. | 0 |  | Price Check Summary: | Small DOL pump - from MSSB power supply and BMS interface provisions | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1752 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1753 | [9 empty] | Zero | 0 | Medium VSD pump - from MSSB power supply and BMS interface provisions | Electrical power supply and controls ( Excluding BMS) to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1754 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1755 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1756 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1757 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | per VSD Fan | 0 | 0 | VSD 11 kW | 1100 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1758 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 3 |  |  | 0 | 0 | 0 | 0 | 0
1759 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1760 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1761 | [11 empty] | Item 8 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1762 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1763 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1764 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1765 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Switchboard Cable 1mm | 0.28 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
1766 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1767 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1768 | [8 empty] | run and fault lights for Medium VSD pump - from MSSB power supply and BMS interface provisions |  |  | Item 15 | run and fault lights, |  |  | run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1769 | [11 empty] | Item 16 | current switch for pump status, |  |  |  | 0 | Nill | 0 | 0 | Current Switch CCS131 | 19.5 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1770 | [8 empty] | Auto/Off/On switch for Medium VSD pump - from MSSB power supply and BMS interface provisions |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1771 | [11 empty] | Item 18 | BMS terminals for on/off control, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1772 | [11 empty] | Item 19 | trefolyte labelling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1773 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Commissioning 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1774 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1775 | Shopping List | Medium VSD pump - from MSSB power supply and BMS interface provisions | MSSB |  |  | 2 |  | Electrical power supply and controls ( Excluding BMS) to Zero (0) Medium VSD pump - from MSSB power supply and BMS interface provisions. This includes supply and install of power and controls. Power for system includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, Controls for system includes: controls cabling, contactors/relays, run and fault lights, current switch for pump status, Auto/Off/On switch, BMS terminals for on/off control, trefolyte labelling, and commissioning/testing. | 0 |  | Price Check Summary: | Medium VSD pump - from MSSB power supply and BMS interface provisions | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1776 | Shopping List | [5 empty] | 0 | Smoke Management |  | Smoke Management | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0
1777 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1778 | [9 empty] | Zero | 0 | smoke exhaust systems | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1779 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1780 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1781 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Fan < 3m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 1.5 |  |  | 0 | 0 | 0 | 0 | 0
1782 | [11 empty] | Item 4 | Danfoss VSD ( with internal program for stair press control), |  |  |  | 0 | Nill | 0 | 0 | VSD Stair Press 7.5kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1783 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | FRC3025+E 2 hour fire for stair p | 4.83 | 0 | 0 | 0 | 15 |  |  | 0 | 0 | 0 | 0 | 0
1784 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1785 | [11 empty] | Item 7 | 003 padlock, |  |  |  | 0 | Nill | 0 | 0 | 003 Keyed Padlocks | 30 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1786 | [11 empty] | Item 8 | fan isolator and MSSB AS1668.1 trefolyte label. |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1787 | [11 empty] | Item 9 | Controls for systems includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | FRC3025+E 2 hour fire for stair p | 4.83 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1788 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1789 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1790 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1791 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1792 | [11 empty] | Item 14 | air pressure switch, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1793 | [8 empty] | Run and fault lights for smoke exhaust systems |  |  | Item 15 | run light, |  |  | Run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1794 | [11 empty] | Item 16 | fault light, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1795 | [8 empty] | Auto/Off/On switch for smoke exhaust systems |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1796 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1797 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface at MSSB for fire trade connection | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1798 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1799 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1800 | Shopping List | smoke exhaust systems | EITHER |  |  |  |  | Electrical power supply and controls to Zero (0) smoke exhaust systems. This includes supply and install of power and controls. Power for systems includes: CB, cabling to VSD, Danfoss VSD ( with internal program for stair press control), shielded cabling, local isolator, 003 padlock, fan isolator and MSSB AS1668.1 trefolyte label. Controls for systems includes: controls cabling, contactors/relays, air pressure switch, run light, fault light, Auto/Off/On switch, interface at MSSB for fire trade connection and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | smoke exhaust systems | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1801 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1802 | [9 empty] | Zero | 0 | stair pressurisation systems | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1803 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1804 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1805 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Fan < 3m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 1.5 |  |  | 0 | 0 | 0 | 0 | 0
1806 | [11 empty] | Item 4 | Danfoss VSD ( with internal program for stair press control), |  |  |  | 0 | Nill | 0 | 0 | VSD Stair Press 7.5kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1807 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | FRC3025+E 2 hour fire for stair p | 4.83 | 0 | 0 | 0 | 15 |  |  | 0 | 0 | 0 | 0 | 0
1808 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1809 | [11 empty] | Item 7 | 003 padlock, |  |  |  | 0 | Nill | 0 | 0 | 003 Keyed Padlocks | 30 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1810 | [11 empty] | Item 8 | fan isolator and MSSB AS1668.1 trefolyte label. |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1811 | [11 empty] | Item 9 | Controls for systems includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | FRC3025+E 2 hour fire for stair p | 4.83 | 0 | 0 | 0 | 40 |  |  | 0 | 0 | 0 | 0 | 0
1812 | [8 empty] | additional stairwell pressure transducers (for redundancy should one fail) for stair pressurisation systems |  |  | Item 10 | Stairwell pressure transducers ( 2 per fan for averaging), |  |  | additional stairwell pressure transducers (for redundancy should one fail) | 0 | Misc Install - 1hr | 0 | 0 | Stair press sensor | 100 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1813 | [11 empty] | Item 11 | pressure sensing tubing, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Tubing - 1m | 0 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1814 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1815 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1816 | [11 empty] | Item 14 | air pressure switch, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1817 | [8 empty] | Run and fault lights for stair pressurisation systems |  |  | Item 15 | run light, |  |  | Run and fault lights | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1818 | [11 empty] | Item 16 | fault light, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1819 | [8 empty] | Auto/Off/On switch for stair pressurisation systems |  |  | Item 17 | Auto/Off/On switch, |  |  | Auto/Off/On switch | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1820 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1821 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface at MSSB for fire trade connection | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1822 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1823 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1824 | Shopping List | stair pressurisation systems | EITHER |  |  |  |  | Electrical power supply and controls to Zero (0) stair pressurisation systems. This includes supply and install of power and controls. Power for systems includes: CB, cabling to VSD, Danfoss VSD ( with internal program for stair press control), shielded cabling, local isolator, 003 padlock, fan isolator and MSSB AS1668.1 trefolyte label. Controls for systems includes: Stairwell pressure transducers ( 2 per fan for averaging), pressure sensing tubing, controls cabling, contactors/relays, air pressure switch, run light, fault light, Auto/Off/On switch, interface at MSSB for fire trade connection and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | stair pressurisation systems | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1825 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1826 | [9 empty] | Zero | 0 | lobby relief system ( including on floor relief dampers) | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | Cost Per Item | Cost for all items | 0 | 0 | 1 | Nill | Cost Per Item | Cost for all items | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1827 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1828 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1829 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Fan < 3m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 1.5 |  |  | 0 | 0 | 0 | 0 | 0
1830 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | Nill | 0 | 0 | VSD Stair Press 7.5kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1831 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | FRC3025+E 2 hour fire for stair p | 4.83 | 0 | 0 | 0 | 15 |  |  | 0 | 0 | 0 | 0 | 0
1832 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1833 | [11 empty] | Item 7 | 003 padlock, |  |  |  | 0 | Nill | 0 | 0 | 003 Keyed Padlocks | 30 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1834 | [11 empty] | Item 8 | fan isolator and MSSB AS1668.1 trefolyte labels. |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1835 | [11 empty] | Item 9 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 40 |  |  | 0 | 0 | 0 | 0 | 0
1836 | [11 empty] | Item 10 | fire relay per floor for fire interface, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 9 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1837 | [11 empty] | Item 11 | relief damper actuators ( 1 per floor) including cabling, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Spring return damper actuator | 200 | 0 | 0 | 0 | 9 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 180 |  |  | 0 | 0 | 0 | 0 | 0
1838 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1839 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1840 | [11 empty] | Item 14 | air pressure switch, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1841 | [11 empty] | Item 15 | pressure transducers ( 1 per fan ), |  |  |  | 0 | Nill | 0 | 0 | Stair press sensor | 100 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1842 | [11 empty] | Item 16 | run and fault light, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1843 | [11 empty] | Item 17 | Auto/Off/On switch, |  |  |  | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1844 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1845 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface at MSSB for fire trade connection | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1846 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1847 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1848 | Shopping List | lobby relief system ( including on floor relief dampers) | EITHER |  |  |  |  | Electrical power supply and controls to Zero (0) lobby relief system ( including on floor relief dampers). This includes supply and install of power and controls. Power for system includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, 003 padlock, fan isolator and MSSB AS1668.1 trefolyte labels. Controls for system includes: fire relay per floor for fire interface, relief damper actuators ( 1 per floor) including cabling, controls cabling, contactors/relays, air pressure switch, pressure transducers ( 1 per fan ), run and fault light, Auto/Off/On switch, interface at MSSB for fire trade connection and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | lobby relief system ( including on floor relief dampers) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1849 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1850 | [9 empty] | Zero | 0 | Fire essential spring return damper actuator | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1851 | [11 empty] | Item 1 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1852 | [11 empty] | Item 2 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1853 | [11 empty] | Item 3 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1854 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1855 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1856 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1857 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1858 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1859 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1860 | [11 empty] | Item 10 | Spring return damper actuator ( Nominal allowance of 2 per system for smoke control - TBC in detailed design), |  |  |  | 0 | Nill | 0 | 0 | Spring return damper actuator | 200 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1861 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1862 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | FRC3025+E 2 hour fire for stair p | 4.83 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1863 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1864 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1865 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1866 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1867 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1868 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1869 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface at MSSB for fire trade connection | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1870 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1871 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1872 | Shopping List | Fire essential spring return damper actuator | EITHER |  |  |  |  | Electrical power supply and controls to Zero (0) Fire essential spring return damper actuator. This includes supply and install of Spring return damper actuator ( Nominal allowance of 2 per system for smoke control - TBC in detailed design), controls cabling, interface at MSSB for fire trade connection and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | Fire essential spring return damper actuator | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1873 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1874 | [9 empty] | Zero | 0 | Smoke Exhaust system ( including on floor dampers) | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | Cost Per Item | Cost for all items | 0 | 0 | 1 | Nill | Cost Per Item | Cost for all items | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1875 | [11 empty] | Item 1 | power and controls. Power for system includes: |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1876 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1877 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Fan < 3m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 1.5 |  |  | 0 | 0 | 0 | 0 | 0
1878 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | Nill | 0 | 0 | VSD Stair Press 7.5kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1879 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | FRC3025+E 2 hour fire for stair p | 4.83 | 0 | 0 | 0 | 15 |  |  | 0 | 0 | 0 | 0 | 0
1880 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1881 | [11 empty] | Item 7 | 003 padlock, |  |  |  | 0 | Nill | 0 | 0 | 003 Keyed Padlocks | 30 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1882 | [11 empty] | Item 8 | fan isolator and MSSB AS1668.1 trefolyte labels. |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1883 | [11 empty] | Item 9 | Controls for system includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 40 |  |  | 0 | 0 | 0 | 0 | 0
1884 | [11 empty] | Item 10 | fire relay per floor for fire interface, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 4 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1885 | [11 empty] | Item 11 | relief damper actuators ( 1 per floor) including cabling, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Spring return damper actuator | 200 | 0 | 0 | 0 | 4 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 180 |  |  | 0 | 0 | 0 | 0 | 0
1886 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1887 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1888 | [11 empty] | Item 14 | air pressure switch, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1889 | [11 empty] | Item 15 | pressure transducers ( 1 per fan ), |  |  |  | 0 | Nill | 0 | 0 | Stair press sensor | 100 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1890 | [11 empty] | Item 16 | run and fault light, |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1891 | [11 empty] | Item 17 | Auto/Off/On switch, |  |  |  | 0 | Nill | 0 | 0 | AOM Switches | 57.95 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1892 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1893 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface at MSSB for fire trade connection | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1894 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1895 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1896 | Shopping List | Smoke Exhaust system ( including on floor dampers) | EITHER |  |  |  | 0 | Electrical power supply and controls to Zero (0) Smoke Exhaust system ( including on floor dampers). This includes supply and install of power and controls. Power for system includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, 003 padlock, fan isolator and MSSB AS1668.1 trefolyte labels. Controls for system includes: fire relay per floor for fire interface, relief damper actuators ( 1 per floor) including cabling, controls cabling, contactors/relays, air pressure switch, pressure transducers ( 1 per fan ), run and fault light, Auto/Off/On switch, interface at MSSB for fire trade connection and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | fire cabling from FIP. | Price Check Summary: | Smoke Exhaust system ( including on floor dampers) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1897 | Shopping List | [5 empty] | 1 | Kitchen |  | Kitchen | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0
1898 | [34 empty] | 0 | 0 | 0 | 0 | 0
1899 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1900 | [9 empty] | Zero | 0 | Kitchen Hood Make Up Supply Sytem ( from local power supply) | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1901 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1902 | [11 empty] | Item 2 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1903 | [7 empty] | Coordination Note: - Electrical trade: Please refer to our exclusions relating to Power suply adjacent fan |  |  |  | Item 3 | cabling to VSD ( from local isolator), | Electrical trade | Power suply adjacent fan |  | 0 | Fan < 3m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 1.5 |  |  | 0 | 0 | 0 | 0 | 0
1904 | [11 empty] | Item 4 | Danfoss VSD ( interconnected to ramp with kitchen exhaust VSD), |  |  |  | 0 | Nill | 0 | 0 | VSD Car Park 3kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1905 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 15 |  |  | 0 | 0 | 0 | 0 | 0
1906 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1907 | [11 empty] | Item 7 | Controls for systems includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1908 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1909 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1910 | [11 empty] | Item 10 | air pressure switch, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1911 | [11 empty] | Item 11 | trefolyte labeling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1912 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 40 |  |  | 0 | 0 | 0 | 0 | 0
1913 | [11 empty] | Item 13 |  |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1914 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1915 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 4 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1916 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1917 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1918 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1919 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP to VSD |  |  |  | Item 19 | interface for fire trade connection available at VSD, | Fire trade | fire cabling from FIP to VSD |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1920 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1921 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1922 | Shopping List | Kitchen Hood Make Up Supply Sytem ( from local power supply) | LOCAL |  |  |  |  | Electrical power supply and controls to Zero (0) Kitchen Hood Make Up Supply Sytem ( from local power supply). This includes supply and install of power and controls. Power for systems includes: cabling to VSD ( from local isolator), Danfoss VSD ( interconnected to ramp with kitchen exhaust VSD), shielded cabling, local isolator, Controls for systems includes: air pressure switch, trefolyte labeling, controls cabling, interface for fire trade connection available at VSD, and commissioning/testing. Coordination Note: - Electrical trade: Please refer to our exclusions relating to Power suply adjacent fanCoordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP to VSD | 0 | Power suply adjacent fanfire cabling from FIP to VSD | Price Check Summary: | Kitchen Hood Make Up Supply Sytem ( from local power supply) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1923 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1924 | [9 empty] | Zero | 0 | Kitchen Hood Make Up Supply Sytem ( from MSSB power supply) | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1925 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1926 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1927 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 1.5 |  |  | 0 | 0 | 0 | 0 | 0
1928 | [11 empty] | Item 4 | Danfoss VSD ( interconnected to ramp with kitchen exhaust VSD), |  |  |  | 0 | Nill | 0 | 0 | VSD Car Park 3kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1929 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
1930 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1931 | [11 empty] | Item 7 | Controls for systems includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1932 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1933 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1934 | [11 empty] | Item 10 | air pressure switch, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1935 | [11 empty] | Item 11 | trefolyte labeling, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1936 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 40 |  |  | 0 | 0 | 0 | 0 | 0
1937 | [11 empty] | Item 13 |  |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1938 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1939 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 4 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1940 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1941 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1942 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1943 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP to MSSB |  |  |  | Item 19 | interface for fire trade connection available at MSSB, | Fire trade | fire cabling from FIP to MSSB |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1944 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1945 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1946 | Shopping List | Kitchen Hood Make Up Supply Sytem ( from MSSB power supply) | MSSB |  |  |  |  | Electrical power supply and controls to Zero (0) Kitchen Hood Make Up Supply Sytem ( from MSSB power supply). This includes supply and install of power and controls. Power for systems includes: CB, cabling to VSD, Danfoss VSD ( interconnected to ramp with kitchen exhaust VSD), shielded cabling, local isolator, Controls for systems includes: air pressure switch, trefolyte labeling, controls cabling, interface for fire trade connection available at MSSB, and commissioning/testing. Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP to MSSB | 0 | fire cabling from FIP to MSSB | Price Check Summary: | Kitchen Hood Make Up Supply Sytem ( from MSSB power supply) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1947 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1948 | [9 empty] | Zero | 0 | Kitchen Exhaust Sytem ( from local power supply with 2 separate switchplates) | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1949 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 0 | per VSD Fan | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1950 | [11 empty] | Item 2 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1951 | [7 empty] | Coordination Note: - Electrical trade: Please refer to our exclusions relating to Power suply adjacent fan |  |  |  | Item 3 | cabling to VSD ( from local isolator), | Electrical trade | Power suply adjacent fan |  | 0 | Fan < 3m cable | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 1.5 |  |  | 0 | 0 | 0 | 0 | 0
1952 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 0 | Nill | 0 | 0 | VSD Car Park 3kW | 750 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1953 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 15 |  |  | 0 | 0 | 0 | 0 | 0
1954 | [11 empty] | Item 6 | local isolator, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1955 | [11 empty] | Item 7 | Controls for systems includes: |  |  |  | 0 | Control panel | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1956 | [11 empty] | Item 8 | controls enclosure, |  |  |  | 0 | Nill | 0 | 0 | Control box - Plastic | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1957 | [11 empty] | Item 9 | 24v transformer to ensure all wiring within wet area is extra low voltage, |  |  |  | 0 | Nill | 0 | 0 | Controls transformer | 47 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1958 | [11 empty] | Item 10 | air pressure switch, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Air Pressure switch | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1959 | [11 empty] | Item 11 | trefolyte labeling in compliance with AS1668, |  |  |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1960 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 40 |  |  | 0 | 0 | 0 | 0 | 0
1961 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1962 | [11 empty] | Item 14 | 2 separate 316 stainless steel switchplates installed in kitchen, |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Stainless switchplate - 4 switches | 350 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1963 | [11 empty] | Item 15 | run and fault lights (mounted in kitchen switchplate), |  |  |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 4 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1964 | [11 empty] | Item 16 | start puchbutton (mounted in kitchen switchplate), |  |  |  | 0 | Nill | 0 | 0 | push button switch | 9.55 | 0 | 0 | 0 | 2 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1965 | [11 empty] | Item 17 | speed control dial (total of 1 mounted in kitchen switchplate), |  |  |  | 0 | Nill | 0 | 0 | speed control dial | 30 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1966 | [7 empty] | Coordination Note: - Hydraulics/Kichen trade: Please refer to our exclusions relating to supply and install of gas solenoid |  |  |  | Item 18 | relay, cabling and connection to gas solenoid, | Hydraulics/Kichen trade | supply and install of gas solenoid |  | 0 | Misc Install - 1hr | 0 | 0 | Fire Relay | 24.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1967 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface for fire trade connection, | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1968 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1969 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
1970 | Shopping List | Kitchen Exhaust Sytem ( from local power supply with 2 separate switchplates) | LOCAL |  |  |  | 0 | Electrical power supply and controls to Zero (0) Kitchen Exhaust Sytem ( from local power supply with 2 separate switchplates). This includes supply and install of power and controls. Power for systems includes: cabling to VSD ( from local isolator), Danfoss VSD, shielded cabling, local isolator, Controls for systems includes: controls enclosure, 24v transformer to ensure all wiring within wet area is extra low voltage, air pressure switch, trefolyte labeling in compliance with AS1668, controls cabling, contactors/relays, 2 separate 316 stainless steel switchplates installed in kitchen, run and fault lights (mounted in kitchen switchplate), start puchbutton (mounted in kitchen switchplate), speed control dial (total of 1 mounted in kitchen switchplate), relay, cabling and connection to gas solenoid, interface for fire trade connection, and commissioning/testing. Coordination Note: - Electrical trade: Please refer to our exclusions relating to Power suply adjacent fanCoordination Note: - Hydraulics/Kichen trade: Please refer to our exclusions relating to supply and install of gas solenoidCoordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | Power suply adjacent fansupply and install of gas solenoidfire cabling from FIP. | Price Check Summary: | Kitchen Exhaust Sytem ( from local power supply with 2 separate switchplates) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
1971 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1972 | [9 empty] | one | 1 | Kitchen Exhaust Sytem (from MSSB) | Electrical power supply and controls to | By | Exclusions |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1973 | [11 empty] | Item 1 | power and controls. Power for systems includes: |  |  |  | 1 | per VSD Fan | 1 | 1.5 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 |  |  |  | 0 | 0 | 0 | 0 | 0
1974 | [11 empty] | Item 2 | CB, |  |  |  | 1 | Nill | 1 | 0 | CB 3 Phase 25A | 36.2 | 36.2 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1975 | [11 empty] | Item 3 | cabling to VSD, |  |  |  | 1 | Cabling 10-20m | 1 | 2 | Nill | 0 | 0 | 1 | 1 | 1 | 4mm Cable 3 core and Earth | 2.9 | 4.35 | 1.5 | 1 | 1.5 |  |  | 0 | 0 | 0 | 0 | 0
1976 | [11 empty] | Item 4 | Danfoss VSD, |  |  |  | 1 | Nill | 1 | 0 | VSD Car Park 3kW | 750 | 750 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1977 | [11 empty] | Item 5 | shielded cabling, |  |  |  | 1 | Nill | 1 | 0 | Nill | 0 | 0 | 1 | 1 | 1 | 4mm Cable 3 core and Earth | 2.9 | 43.5 | 15 | 1 | 15 |  |  | 0 | 0 | 0 | 0 | 0
1978 | [11 empty] | Item 6 | local isolator, |  |  |  | 1 | Nill | 1 | 0 | 3 phase isolator 63A WP363 | 38.72 | 38.72 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1979 | [11 empty] | Item 7 | Controls for systems includes: |  |  |  | 1 | Control panel | 1 | 2 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1980 | [11 empty] | Item 8 | controls enclosure, |  |  |  | 1 | Nill | 1 | 0 | Control box - Plastic | 50 | 50 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1981 | [11 empty] | Item 9 | 24v transformer to ensure all wiring within wet area is extra low voltage, |  |  |  | 1 | Nill | 1 | 0 | Controls transformer | 47 | 47 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1982 | [11 empty] | Item 10 | air pressure switch, |  |  |  | 1 | Misc Install - 1hr | 1 | 1 | Air Pressure switch | 50 | 50 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1983 | [11 empty] | Item 11 | trefolyte labeling in compliance with AS1668, |  |  |  | 1 | Nill | 1 | 0 | trefolite | 300 | 300 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1984 | [11 empty] | Item 12 | controls cabling, |  |  |  | 1 | Misc Install - 1hr | 1 | 1 | Nill | 0 | 0 | 1 | 1 | 1 | 7030 2 pair TCAS7302P | 0.88 | 35.2 | 40 | 1 | 40 |  |  | 0 | 0 | 0 | 0 | 0
1985 | [11 empty] | Item 13 | contactors/relays, |  |  |  | 1 | Contactors | 1 | 1 | Contactors + OL | 91.05 | 91.05 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1986 | [11 empty] | Item 14 | 316 stainless steel switchplate installed in kitchen, |  |  |  | 1 | Misc Install - 2hr | 1 | 2 | Stainless switchplate - 4 switches | 350 | 350 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1987 | [11 empty] | Item 15 | run and fault lights (mounted in kitchen switchplate), |  |  |  | 1 | Nill | 1 | 0 | run and fault leds | 16 | 32 | 2 | 1 | 2 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1988 | [11 empty] | Item 16 | start pushbutton (mounted in kitchen switchplate), |  |  |  | 1 | Nill | 1 | 0 | push button switch | 9.55 | 9.55 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1989 | [11 empty] | Item 17 | speed control dial (mounted in kitchen switchplate), |  |  |  | 1 | Nill | 1 | 0 | speed control dial | 30 | 30 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1990 | [7 empty] | Coordination Note: - Hydraulics/Kichen trade: Please refer to our exclusions relating to supply and install of gas solenoid |  |  |  | Item 18 | relay, cabling and connection to gas solenoid, | Hydraulics/Kichen trade | supply and install of gas solenoid |  | 1 | Misc Install - 1hr | 1 | 1 | Fire Relay | 24.2 | 24.2 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1991 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | interface for fire trade connection, | Fire trade | fire cabling from FIP. |  | 1 | Nill | 1 | 0 | Interface for fire trade fan control | 40 | 40 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1992 | [11 empty] | Item 20 | and commissioning/testing. |  |  |  | 1 | Misc Install - 1hr | 1 | 1 | Nill | 0 | 0 | 1 | 1 | 1 | Nill | 0 | 0 | 0 | 1 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1993 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 2931.77 |  |  |  | Total Labour Cost | 1000 | 12.5 | Total Materials item 1 cost |  | 1848.72 |  |  |  | Total continuous material cost |  | 83.05 |  |  |  | 2931.77 |  | 0 | 0 | 0 | 0 | 0
1994 | Shopping List | Kitchen Exhaust Sytem (from MSSB) | MSSB |  |  |  | 1 | Electrical power supply and controls to one (1) Kitchen Exhaust Sytem (from MSSB). This includes supply and install of power and controls. Power for systems includes: CB, cabling to VSD, Danfoss VSD, shielded cabling, local isolator, Controls for systems includes: controls enclosure, 24v transformer to ensure all wiring within wet area is extra low voltage, air pressure switch, trefolyte labeling in compliance with AS1668, controls cabling, contactors/relays, 316 stainless steel switchplate installed in kitchen, run and fault lights (mounted in kitchen switchplate), start pushbutton (mounted in kitchen switchplate), speed control dial (mounted in kitchen switchplate), relay, cabling and connection to gas solenoid, interface for fire trade connection, and commissioning/testing. Coordination Note: - Hydraulics/Kichen trade: Please refer to our exclusions relating to supply and install of gas solenoidCoordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 2931.77 | supply and install of gas solenoidfire cabling from FIP. | Price Check Summary: | Kitchen Exhaust Sytem (from MSSB) | Average cost per system | 2931.77 |  |  |  | Average hrs per system |  | 12.5 | Average cost per system |  | 1848.72 |  |  |  | Average cost per system |  | 83.05 |  |  |  |  | 3664.7125 | 2931.77 | 1000 | 1848.72 | 83.05 | 0
1995 | Shopping List | [5 empty] | 0 | Other |  | Other | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0
1996 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
1997 | [9 empty] | Zero | 0 | Electric Duct Heater ( 3 phase -Exclude Field cabling, SSRs and HPT) | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
1998 | [11 empty] | Item 1 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
1999 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 phase 50A (aprox size) | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2000 | [11 empty] | Item 3 | HPT cabling and power cabling into MSSB, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
2001 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2002 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2003 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2004 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2005 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to heater trefolyte label. |  |  |  | Item 8 |  | Customers in-house electrician | heater trefolyte label. |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2006 | [11 empty] | Item 9 | Controls for systems includes: |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2007 | [11 empty] | Item 10 | SSR and BMS interface to allow modulating control ( 1 per phase), | BMS trade |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 3 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2008 | [11 empty] | Item 11 | heater protection thermostat ( including cabling back to MSSB and interlock relay), |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2009 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
2010 | [11 empty] | Item 13 | contactors/relays ( per phase), |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2011 | [11 empty] | Item 14 | interface with ahu air pressure switch, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2012 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2013 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Power cabling from MSSB to heater and HPT. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  |  |  | Item 16 | HPT fault light, | Customers in-house electrician | Power cabling from MSSB to heater and HPT. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2014 | [7 empty] | Coordination Note: - BMS trade: Please refer to our exclusions relating to cabling from MSSB's to BMS system |  |  |  | Item 17 | BMS terminals for HPT fault indication, | BMS trade | cabling from MSSB's to BMS system |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2015 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2016 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence), | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2017 | [7 empty] | Coordination Note: - : Please refer to our exclusions relating to 0 |  |  |  | Item 20 | Documented test results of final electrical systems and Form 16 certification. |  | 0 |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2018 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
2019 | Shopping List | Electric Duct Heater ( 3 phase -Exclude Field cabling, SSRs and HPT) | MSSB |  |  |  |  | Electrical power supply and controls to Zero (0) Electric Duct Heater ( 3 phase -Exclude Field cabling, SSRs and HPT). This includes supply and install of CB, HPT cabling and power cabling into MSSB, Controls for systems includes: SSR and BMS interface to allow modulating control ( 1 per phase), heater protection thermostat ( including cabling back to MSSB and interlock relay), controls cabling, contactors/relays ( per phase), interface with ahu air pressure switch, HPT fault light, BMS terminals for HPT fault indication, testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence), Documented test results of final electrical systems and Form 16 certification. Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to heater trefolyte label. Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Power cabling from MSSB to heater and HPT. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. Coordination Note: - BMS trade: Please refer to our exclusions relating to cabling from MSSB's to BMS system Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. Coordination Note: - : Please refer to our exclusions relating to 0 | 0 | heater trefolyte label. Power cabling from MSSB to heater and HPT. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. cabling from MSSB's to BMS system fire cabling from FIP. 0 | Price Check Summary: | Electric Duct Heater ( 3 phase -Exclude Field cabling, SSRs and HPT) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
2020 | [8 empty] | Extras |  | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
2021 | [9 empty] | Zero | 0 | Electric Duct Heater ( 3 phase -Exclude Field cabling) | Electrical power supply and controls to | By | Exclusions |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2022 | [11 empty] | Item 1 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
2023 | [11 empty] | Item 2 | CB, |  |  |  | 0 | Nill | 0 | 0 | CB 3 phase 50A (aprox size) | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2024 | [11 empty] | Item 3 | connections of both HPT cabling and power cabling into MSSB, |  |  |  | 0 | Cabling 10-20m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 4mm Cable 3 core and Earth | 2.9 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
2025 | [11 empty] | Item 4 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2026 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2027 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2028 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2029 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to heater trefolyte label. |  |  |  | Item 8 |  | Customers in-house electrician | heater trefolyte label. |  | 0 | Nill | 0 | 0 | trefolite | 300 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2030 | [11 empty] | Item 9 | Controls for systems includes: |  |  |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2031 | [7 empty] | Coordination Note: - BMS trade: Please refer to our exclusions relating to cabling from MSSB's to BMS system |  |  |  | Item 10 | SSR and BMS interface to allow modulating control ( 1 per phase), | BMS trade | cabling from MSSB's to BMS system |  | 0 | Nill | 0 | 0 | SSR ( 1 phase) | 50 | 0 | 0 | 0 | 3 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2032 | [11 empty] | Item 11 | heater protection thermostat ( including cabling back to MSSB and interlock relay), |  |  |  | 0 | Misc Install - 1hr | 0 | 0 | HPT | 150 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2033 | [11 empty] | Item 12 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
2034 | [11 empty] | Item 13 | contactors/relays ( per phase), |  |  |  | 0 | Contactors | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2035 | [11 empty] | Item 14 | interface with ahu air pressure switch, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2036 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2037 | [7 empty] | Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Power cabling from MSSB to heater and HPT. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  |  |  | Item 16 | HPT fault light, | Customers in-house electrician | Power cabling from MSSB to heater and HPT. Customers electrician to leave tails adjacent MSSB for Controlworks to connect. |  | 0 | Nill | 0 | 0 | run and fault leds | 16 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2038 | [7 empty] | Coordination Note: - BMS trade: Please refer to our exclusions relating to cabling from MSSB's to BMS system |  |  |  | Item 17 | BMS terminals for HPT fault indication, | BMS trade | cabling from MSSB's to BMS system |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2039 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2040 | [7 empty] | Coordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. |  |  |  | Item 19 | testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence), | Fire trade | fire cabling from FIP. |  | 0 | Nill | 0 | 0 | Interface for fire trade fan control | 40 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2041 | [11 empty] | Item 20 | Documented test results of final electrical systems and Form 16 certification. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2042 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
2043 | Shopping List | Electric Duct Heater ( 3 phase -Exclude Field cabling) | MSSB |  |  | 28 |  | Electrical power supply and controls to Zero (0) Electric Duct Heater ( 3 phase -Exclude Field cabling). This includes supply and install of CB, connections of both HPT cabling and power cabling into MSSB, Controls for systems includes: SSR and BMS interface to allow modulating control ( 1 per phase), heater protection thermostat ( including cabling back to MSSB and interlock relay), controls cabling, contactors/relays ( per phase), interface with ahu air pressure switch, HPT fault light, BMS terminals for HPT fault indication, testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence), Documented test results of final electrical systems and Form 16 certification. Coordination Note: - Customers in-house electrician: Please refer to our exclusions relating to heater trefolyte label. Coordination Note: - BMS trade: Please refer to our exclusions relating to cabling from MSSB's to BMS systemCoordination Note: - Customers in-house electrician: Please refer to our exclusions relating to Power cabling from MSSB to heater and HPT. Customers electrician to leave tails adjacent MSSB for Controlworks to connect.Coordination Note: - BMS trade: Please refer to our exclusions relating to cabling from MSSB's to BMS systemCoordination Note: - Fire trade: Please refer to our exclusions relating to fire cabling from FIP. | 0 | heater trefolyte label. cabling from MSSB's to BMS systemPower cabling from MSSB to heater and HPT. Customers electrician to leave tails adjacent MSSB for Controlworks to connect.cabling from MSSB's to BMS systemfire cabling from FIP. | Price Check Summary: | Electric Duct Heater ( 3 phase -Exclude Field cabling) | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
2044 |  | Item |  |  |  |  | QTY |  | Cost | Exclusions Suggested Words | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
2045 | [9 empty] | Zero | 0 | Motion Sensor ( with internal run on timer) with interlock with other system | Electrical power supply and controls cabling for | By | Exclusions |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2046 | [11 empty] | Item 1 | controls cabling, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2047 | [11 empty] | Item 2 | power supply, |  |  |  | 0 | Nill | 0 | 0 | Motion sensor with run on timer | 200 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
2048 | [11 empty] | Item 3 | contactors/relays |  |  |  | 0 | Nill | 0 | 0 | General Relay | 24.2 | 0 | 0 | 0 | 1 | 7030 2 pair TCAS7302P | 0.88 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
2049 | [11 empty] | Item 4 | and enclosure. |  |  |  | 0 | Nill | 0 | 0 | Control box - Plastic | 50 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2050 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2051 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2052 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2053 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2054 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2055 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2056 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2057 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
2058 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2059 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2060 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2061 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2062 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2063 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2064 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2065 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2066 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
2067 | Shopping List | Motion Sensor ( with internal run on timer) with interlock with other system | Either |  |  |  |  | Electrical power supply and controls cabling for Zero (0) Motion Sensor ( with internal run on timer) with interlock with other system. This includes supply and install of controls cabling, power supply, contactors/relays and enclosure. | 0 |  | Price Check Summary: | Motion Sensor ( with internal run on timer) with interlock with other system | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
2068 |  | Item |  |  |  |  | QTY |  | Cost | Exclusions Suggested Words | Number off systems | System Description | Inclusions | Exclusions |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
2069 | [9 empty] | Zero | 0 | Humidifier | Electrical power supply and controls cabling for | By | Exclusions |  | 0 | Misc Install - 2hr | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2070 | [11 empty] | Item 1 | circuit breaker, |  |  |  | 0 | Nill | 0 | 0 | 3 phase isolator 63A WP363 | 38.72 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2071 | [11 empty] | Item 2 | power supply from MSSB, |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | 2.5mm Twin and Earth | 0.85 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
2072 | [11 empty] | Item 3 | contactors/relays, |  |  |  | 0 | Nill | 0 | 0 | Contactors + OL | 91.05 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 20 |  |  | 0 | 0 | 0 | 0 | 0
2073 | [11 empty] | Item 4 | isolator at unit. |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2074 | [11 empty] | Item 5 |  |  |  |  | 0 | Nill | 0 | 0 | CB 3 Phase 25A | 36.2 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2075 | [11 empty] | Item 6 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2076 | [11 empty] | Item 7 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2077 | [11 empty] | Item 8 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2078 | [11 empty] | Item 9 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2079 | [11 empty] | Item 10 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2080 | [11 empty] | Item 11 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2081 | [11 empty] | Item 12 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
2082 | [11 empty] | Item 13 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2083 | [11 empty] | Item 14 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2084 | [11 empty] | Item 15 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2085 | [11 empty] | Item 16 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2086 | [11 empty] | Item 17 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2087 | [11 empty] | Item 18 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2088 | [11 empty] | Item 19 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2089 | [11 empty] | Item 20 |  |  |  |  | 0 | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2090 | [7 empty] | Inclusions summary: |  | Exclusions summary |  |  | Total Cost: | 0 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 0 |  |  |  | Total continuous material cost |  | 0 |  |  |  | 0 |  | 0 | 0 | 0 | 0 | 0
2091 | Shopping List | Humidifier | MSSB |  |  |  |  | Electrical power supply and controls cabling for Zero (0) Humidifier. This includes supply and install of circuit breaker, power supply from MSSB, contactors/relays, isolator at unit. | 0 |  | Price Check Summary: | Humidifier | Average cost per system | #DIV/0! |  |  |  | Average hrs per system |  | #DIV/0! | Average cost per system |  | #DIV/0! |  |  |  | Average cost per system |  | #DIV/0! |  |  |  |  | 0 | 0 | 0 | 0 | 0 | 0
2092 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2093 | [34 empty] | 0 | 0 | 0 | 0 | 0
2094 | [8 empty] | Extras |  | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install |  |  | Extras | QTY | Labour Item | Quantity of Labour Items | Hours indication ( for total qty) | Materials Item 1 | Cost Per Item | Cost for all items | Total number required = A x B | A: Number of systems | B: Items per system | Continuous Material ( Cable tray, cable, conduit, catenery) | Cost Per Item | Cost for all items | Total Length ( M) = A x B | A: Number of lengths | B: Length ( m) per item |  |  | 0 | 0 | 0 | 0 | 0
2095 | [9 empty] | an estimated | 0.7 | kilometres of cabling required throughout this project | Supply and install appropriate cabling support/fixings for |  |  |  |  | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
2096 | [10 empty] | 697.5 | Item 1 | cable ladder tray, |  |  |  | 0 | 300mm Cable ladder tray install per m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Ladder Tray 300mm wid per metre | 97.5 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
2097 | [11 empty] | Item 2 | cable tray, |  |  |  | 0 | 80mm Cable ladder tray install per m | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Cable Tray 80mm wide 2.4mtr | 18 | 0 | 0 | 0 | 1 |  |  | 0 | 0 | 0 | 0 | 0
2098 | [11 empty] | Item 3 | catenary, conduit |  |  |  | 697.5 | Nill | 697.5 | 0 | Nill | 0 | 0 | 697.5 | 697.5 | 1 | Catenery/Conduit per metre | 1 | 697.5 | 697.5 | 697.5 | 1 |  |  | 0 | 0 | 0 | 0 | 0
2099 | [11 empty] | Item 4 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
2100 | [11 empty] | Item 5 | and miscellaneous hardware. Support systems will be chosen on a case-by-case basis by our licensed electricians in compliance with AS3000 and design specification. |  |  |  | 700 | Nill | 700 | 0 | Hardware Misc Screws etc per m of cable | 0.5 | 350 | 700 | 700 | 1 | Nill | 0 | 0 | 0 | 700 |  |  |  | 0 | 0 | 0 | 0 | 0
2101 | [11 empty] | Item 6 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
2102 | [11 empty] | Item 7 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
2103 | [11 empty] | Item 8 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
2104 | [11 empty] | Item 9 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
2105 | [11 empty] | Item 10 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
2106 | [11 empty] | Item 11 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
2107 | [11 empty] | Item 12 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
2108 | [11 empty] | Item 13 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 |  |  |  | 0 | 0 | 0 | 0 | 0
2109 | [11 empty] | Item 14 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2110 | [11 empty] | Item 15 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2111 | [11 empty] | Item 16 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2112 | [11 empty] | Item 17 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2113 | [11 empty] | Item 18 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2114 | [11 empty] | Item 19 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2115 | [11 empty] | Item 20 | [5 empty] | Nill | 0 | 0 | Nill | 0 | 0 | 0 | 0 | 1 | Nill | 0 | 0 | 0 | 0 | 0 |  |  | 0 | 0 | 0 | 0 | 0
2116 | [12 empty] | Total Cost: | 1047.5 |  |  |  | Total Labour Cost | 0 | 0 | Total Materials item 1 cost |  | 350 |  |  |  | Total continuous material cost |  | 697.5 |  |  |  | 1047.5 |  | 0 | 0 | 0 | 0 | 0
2117 | Shopping List | [5 empty] | - | Cable Support & Miscellaneous |  | Cable Support & Miscellaneous | [23 empty] | 0 | 0 | 0 | 0 | 0 | 0
2118 | Shopping List |  | EITHER |  |  |  | - | Supply and install appropriate cabling support/fixings for an estimated (0.7) kilometres of cabling required throughout this project. This includes a combination of cable ladder tray, cable tray, catenary, conduit and miscellaneous hardware. Support systems will be chosen on a case-by-case basis by our licensed electricians in compliance with AS3000 and design specification. | 1047.5 |  | Price Check Summary: | kilometres of cabling required throughout this project | Average cost per metre of cable | 1.4964 | [12 empty] | Average cost per system |  | 0.99643 |  |  |  |  | 1309.375 | 1047.5
2119 | Variations | Cable Ladder (M) | EITHER | [18 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2120 | Variations | Cable Tray ( M) | EITHER | [31 empty] | 0 | 0 | 0 | 0 | 0
2121 | [6 empty] | 40 | [27 empty] | 0 | 0 | 0 | 0 | 0
2122 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2123 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2124 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2125 | [7 empty] | Electrical power supply and controls cabling to fifty (50) VRF cassettes. Each includes supply and install of controls cabling, power cabling and conduit fom outdoor unit and local power isolator.Each sytem includes install only of proprietory controller and install only of branch connector boxes interconnect cabling. |  | fifty | 50 | VRF cassettes | Electrical power supply and controls cabling to | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2126 | [11 empty] | Item 1 | controls cabling, |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2127 | [11 empty] | Item 2 | power cabling and conduit fom outdoor unit |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2128 | [11 empty] | Item 3 | and local power isolator. |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2129 | [11 empty] | Item 4 | Each sytem includes install only of proprietory controller |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2130 | [11 empty] | Item 5 | and install only of branch connector boxes interconnect cabling. |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2131 | [11 empty] | Item 6 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2132 | [11 empty] | Item 7 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2133 | [11 empty] | Item 8 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2134 | [11 empty] | Item 9 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2135 | [11 empty] | Item 10 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2136 | [11 empty] | Item 11 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2137 | [11 empty] | Item 12 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2138 | [11 empty] | Item 13 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2139 | [11 empty] | Item 14 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2140 | [11 empty] | Item 15 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2141 | [11 empty] | Item 16 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2142 | [11 empty] | Item 17 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2143 | [11 empty] | Item 18 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2144 | [11 empty] | Item 19 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2145 | [11 empty] | Item 20 |  |  |  |  | 50 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2146 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2147 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2148 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2149 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2150 | [7 empty] | Electrical power supply and controls cabling to one hundred and thirty (130) Ducted VRF fan coil units. Each includes supply and install of controls cabling, power cabling and conduit fom outdoor unit and local power isolator.Each sytem includes install only of proprietory controller and install only of branch connector boxes interconnect cabling. |  | one hundred and thirty | 130 | Ducted VRF fan coil units | Electrical power supply and controls cabling to | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2151 | [11 empty] | Item 1 | controls cabling, |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2152 | [11 empty] | Item 2 | power cabling and conduit fom outdoor unit |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2153 | [11 empty] | Item 3 | and local power isolator. |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2154 | [11 empty] | Item 4 | Each sytem includes install only of proprietory controller |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2155 | [11 empty] | Item 5 | and install only of branch connector boxes interconnect cabling. |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2156 | [11 empty] | Item 6 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2157 | [11 empty] | Item 7 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2158 | [11 empty] | Item 8 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2159 | [11 empty] | Item 9 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2160 | [11 empty] | Item 10 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2161 | [11 empty] | Item 11 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2162 | [11 empty] | Item 12 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2163 | [11 empty] | Item 13 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2164 | [11 empty] | Item 14 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2165 | [11 empty] | Item 15 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2166 | [11 empty] | Item 16 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2167 | [11 empty] | Item 17 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2168 | [11 empty] | Item 18 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2169 | [11 empty] | Item 19 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2170 | [11 empty] | Item 20 |  |  |  |  | 130 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2171 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2172 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2173 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2174 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2175 | [7 empty] | Electrical power supply and controls cabling to sixty (60) single split systems. Each includes supply and install of interconnect controls and power cabling between indoor and outdoor unit, power cabling and conduit fom MSSB /ILU-DB to outdoor unit and local isolator for outdoor unit. Each sytem includes install only of proprietory controller |  | sixty | 60 | single split systems | Electrical power supply and controls cabling to | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2176 | [11 empty] | Item 1 | interconnect controls and power cabling between indoor and outdoor unit, |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2177 | [11 empty] | Item 2 | power cabling and conduit fom MSSB /ILU-DB to outdoor unit |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2178 | [11 empty] | Item 3 | and local isolator for outdoor unit. |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2179 | [11 empty] | Item 4 | Each sytem includes install only of proprietory controller |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2180 | [11 empty] | Item 5 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2181 | [11 empty] | Item 6 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2182 | [11 empty] | Item 7 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2183 | [11 empty] | Item 8 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2184 | [11 empty] | Item 9 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2185 | [11 empty] | Item 10 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2186 | [11 empty] | Item 11 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2187 | [11 empty] | Item 12 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2188 | [11 empty] | Item 13 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2189 | [11 empty] | Item 14 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2190 | [11 empty] | Item 15 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2191 | [11 empty] | Item 16 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2192 | [11 empty] | Item 17 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2193 | [11 empty] | Item 18 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2194 | [11 empty] | Item 19 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2195 | [11 empty] | Item 20 |  |  |  |  | 60 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2196 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2197 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2198 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2199 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2200 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2201 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2202 | [7 empty] | Electrical power supply for four (4) continuously running fans. Each includes supply and install of circuit breaker, cabling and conduit fom MSSB and local isolator. |  | four | 4 | continuously running fans | Electrical power supply for | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2203 | [11 empty] | Item 1 | circuit breaker, |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2204 | [11 empty] | Item 2 | cabling and conduit fom MSSB |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2205 | [11 empty] | Item 3 | and local isolator. |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2206 | [11 empty] | Item 4 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2207 | [11 empty] | Item 5 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2208 | [11 empty] | Item 6 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2209 | [11 empty] | Item 7 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2210 | [11 empty] | Item 8 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2211 | [11 empty] | Item 9 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2212 | [11 empty] | Item 10 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2213 | [11 empty] | Item 11 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2214 | [11 empty] | Item 12 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2215 | [11 empty] | Item 13 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2216 | [11 empty] | Item 14 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2217 | [11 empty] | Item 15 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2218 | [11 empty] | Item 16 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2219 | [11 empty] | Item 17 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2220 | [11 empty] | Item 18 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2221 | [11 empty] | Item 19 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2222 | [11 empty] | Item 20 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2223 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2224 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2225 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2226 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2227 | [7 empty] | Electrical power supply and controls for sixteen (16) timeclock controlled fans. Each includes supply and install of circuit breaker, timeclock controller, control contacts, cabling and conduit fom MSSB and local isolator. |  | sixteen | 16 | timeclock controlled fans | Electrical power supply and controls for | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2228 | [11 empty] | Item 1 | circuit breaker, |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2229 | [11 empty] | Item 2 | timeclock controller, |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2230 | [11 empty] | Item 3 | control contacts, |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2231 | [11 empty] | Item 4 | cabling and conduit fom MSSB |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2232 | [11 empty] | Item 5 | and local isolator. |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2233 | [11 empty] | Item 6 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2234 | [11 empty] | Item 7 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2235 | [11 empty] | Item 8 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2236 | [11 empty] | Item 9 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2237 | [11 empty] | Item 10 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2238 | [11 empty] | Item 11 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2239 | [11 empty] | Item 12 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2240 | [11 empty] | Item 13 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2241 | [11 empty] | Item 14 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2242 | [11 empty] | Item 15 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2243 | [11 empty] | Item 16 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2244 | [11 empty] | Item 17 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2245 | [11 empty] | Item 18 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2246 | [11 empty] | Item 19 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2247 | [11 empty] | Item 20 |  |  |  |  | 16 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2248 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2249 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2250 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2251 | [7 empty] | Electrical power supply and controls for nine (9) fans with local on/off control. Each includes supply and install of circuit breaker, local switch ( complete with indication light, cabeling to MSSB and label), control contacts, cabling and conduit fom MSSB and local power isolator. |  | nine | 9 | fans with local on/off control | Electrical power supply and controls for | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2252 | [11 empty] | Item 1 | circuit breaker, |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2253 | [11 empty] | Item 2 | local switch ( complete with indication light, cabeling to MSSB and label), |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2254 | [11 empty] | Item 3 | control contacts, |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2255 | [11 empty] | Item 4 | cabling and conduit fom MSSB |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2256 | [11 empty] | Item 5 | and local power isolator. |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2257 | [11 empty] | Item 6 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2258 | [11 empty] | Item 7 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2259 | [11 empty] | Item 8 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2260 | [11 empty] | Item 9 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2261 | [11 empty] | Item 10 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2262 | [11 empty] | Item 11 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2263 | [11 empty] | Item 12 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2264 | [11 empty] | Item 13 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2265 | [11 empty] | Item 14 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2266 | [11 empty] | Item 15 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2267 | [11 empty] | Item 16 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2268 | [11 empty] | Item 17 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2269 | [11 empty] | Item 18 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2270 | [11 empty] | Item 19 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2271 | [11 empty] | Item 20 |  |  |  |  | 9 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2272 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2273 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2274 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2275 | [7 empty] | Electrical power supply and controls for six (6) two speed fans with push button boost to high speed. Each includes supply and install of circuit breakers, local switch ( complete with pushbutton, cabeling to MSSB and label), control contacts/relays, cabling and conduit fom MSSB for both speedsand local power isolator. |  | six | 6 | two speed fans with push button boost to high speed | Electrical power supply and controls for | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2276 | [11 empty] | Item 1 | circuit breakers, |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2277 | [11 empty] | Item 2 | local switch ( complete with pushbutton, cabeling to MSSB and label), |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2278 | [11 empty] | Item 3 | control contacts/relays, |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2279 | [11 empty] | Item 4 | cabling and conduit fom MSSB for both speeds |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2280 | [11 empty] | Item 5 | and local power isolator. |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2281 | [11 empty] | Item 6 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2282 | [11 empty] | Item 7 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2283 | [11 empty] | Item 8 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2284 | [11 empty] | Item 9 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2285 | [11 empty] | Item 10 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2286 | [11 empty] | Item 11 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2287 | [11 empty] | Item 12 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2288 | [11 empty] | Item 13 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2289 | [11 empty] | Item 14 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2290 | [11 empty] | Item 15 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2291 | [11 empty] | Item 16 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2292 | [11 empty] | Item 17 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2293 | [11 empty] | Item 18 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2294 | [11 empty] | Item 19 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2295 | [11 empty] | Item 20 |  |  |  |  | 6 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2296 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2297 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2298 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2299 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2300 | [7 empty] | Electrical power supply and controls for two (2) kitchen/café canopy exhaust fans. Each includes supply and install of circuit breakers, LO/OFF/HI local switch ( complete with run light , cabeling to MSSB and label), control contacts/relays, cabling and conduit fom MSSB for both speeds and local power isolator.Gas solenoid interlock is excluded. |  | two | 2 | kitchen/café canopy exhaust fans | Electrical power supply and controls for | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2301 | [11 empty] | Item 1 | circuit breakers, |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2302 | [11 empty] | Item 2 | LO/OFF/HI local switch ( complete with run light , cabeling to MSSB and label), |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2303 | [11 empty] | Item 3 | control contacts/relays, |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2304 | [11 empty] | Item 4 | cabling and conduit fom MSSB for both speeds |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2305 | [11 empty] | Item 5 | and local power isolator. |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2306 | [11 empty] | Item 6 | Gas solenoid interlock is excluded. |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2307 | [11 empty] | Item 7 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2308 | [11 empty] | Item 8 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2309 | [11 empty] | Item 9 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2310 | [11 empty] | Item 10 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2311 | [11 empty] | Item 11 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2312 | [11 empty] | Item 12 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2313 | [11 empty] | Item 13 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2314 | [11 empty] | Item 14 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2315 | [11 empty] | Item 15 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2316 | [11 empty] | Item 16 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2317 | [11 empty] | Item 17 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2318 | [11 empty] | Item 18 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2319 | [11 empty] | Item 19 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2320 | [11 empty] | Item 20 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2321 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2322 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2323 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2324 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2325 | [7 empty] | Electrical power supply and controls for two (2) 2 speed kitchen/cafe canopy supply fan. Each includes supply and install of circuit breakers, interlock with kitchen/canopy exhaust fan but with fire shutdowncontrol contacts/relays, cabling and conduit fom MSSB for both speeds and local power isolator. |  | two | 2 | 2 speed kitchen/cafe canopy supply fan | Electrical power supply and controls for | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2326 | [11 empty] | Item 1 | circuit breakers, |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2327 | [11 empty] | Item 2 | interlock with kitchen/canopy exhaust fan but with fire shutdown |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2328 | [11 empty] | Item 3 | control contacts/relays, |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2329 | [11 empty] | Item 4 | cabling and conduit fom MSSB for both speeds |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2330 | [11 empty] | Item 5 | and local power isolator. |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2331 | [11 empty] | Item 6 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2332 | [11 empty] | Item 7 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2333 | [11 empty] | Item 8 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2334 | [11 empty] | Item 9 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2335 | [11 empty] | Item 10 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2336 | [11 empty] | Item 11 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2337 | [11 empty] | Item 12 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2338 | [11 empty] | Item 13 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2339 | [11 empty] | Item 14 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2340 | [11 empty] | Item 15 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2341 | [11 empty] | Item 16 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2342 | [11 empty] | Item 17 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2343 | [11 empty] | Item 18 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2344 | [11 empty] | Item 19 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2345 | [11 empty] | Item 20 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2346 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2347 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2348 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2349 | [7 empty] | Electrical power supply and controls for one (1) thermostat controlled fan. Each includes supply and install of circuit breakers, local thermostatcontrol contacts/relays, cabling and conduit fom MSSB for both speeds and local power isolator. |  | one | 1 | thermostat controlled fan | Electrical power supply and controls for | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2350 | [11 empty] | Item 1 | circuit breakers, |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2351 | [11 empty] | Item 2 | local thermostat |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2352 | [11 empty] | Item 3 | control contacts/relays, |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2353 | [11 empty] | Item 4 | cabling and conduit fom MSSB for both speeds |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2354 | [11 empty] | Item 5 | and local power isolator. |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2355 | [11 empty] | Item 6 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2356 | [11 empty] | Item 7 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2357 | [11 empty] | Item 8 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2358 | [11 empty] | Item 9 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2359 | [11 empty] | Item 10 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2360 | [11 empty] | Item 11 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2361 | [11 empty] | Item 12 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2362 | [11 empty] | Item 13 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2363 | [11 empty] | Item 14 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2364 | [11 empty] | Item 15 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2365 | [11 empty] | Item 16 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2366 | [11 empty] | Item 17 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2367 | [11 empty] | Item 18 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2368 | [11 empty] | Item 19 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2369 | [11 empty] | Item 20 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2370 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2371 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2372 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2373 | [7 empty] | Electrical power supply and controls for one (1) dryer enclosure fan. Each includes supply and install of circuit breakers, flowsitchcontrol contacts/relays, cabling and conduit fom MSSB for both speeds and local power isolator.This includes interface controls and cabling to gas solenoid valve |  | one | 1 | dryer enclosure fan | Electrical power supply and controls for | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2374 | [11 empty] | Item 1 | circuit breakers, |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2375 | [11 empty] | Item 2 | flowsitch |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2376 | [11 empty] | Item 3 | control contacts/relays, |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2377 | [11 empty] | Item 4 | cabling and conduit fom MSSB for both speeds |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2378 | [11 empty] | Item 5 | and local power isolator. |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2379 | [11 empty] | Item 6 | This includes interface controls and cabling to gas solenoid valve |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2380 | [11 empty] | Item 7 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2381 | [11 empty] | Item 8 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2382 | [11 empty] | Item 9 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2383 | [11 empty] | Item 10 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2384 | [11 empty] | Item 11 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2385 | [11 empty] | Item 12 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2386 | [11 empty] | Item 13 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2387 | [11 empty] | Item 14 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2388 | [11 empty] | Item 15 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2389 | [11 empty] | Item 16 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2390 | [11 empty] | Item 17 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2391 | [11 empty] | Item 18 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2392 | [11 empty] | Item 19 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2393 | [11 empty] | Item 20 |  |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2394 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2395 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2396 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2397 | [7 empty] | Electrical power supply and controls for seven (7) supply fans interlocked with airconditioning. Each includes supply and install of circuit breakers, interlock cabling and controls with AC indoor unitcontrol contacts/relays, cabling and conduit fom MSSBand local power isolator.This excludes supply and installation of AC manufacturers interface card where required. |  | seven | 7 | supply fans interlocked with airconditioning | Electrical power supply and controls for | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2398 | [11 empty] | Item 1 | circuit breakers, |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2399 | [11 empty] | Item 2 | interlock cabling and controls with AC indoor unit |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2400 | [11 empty] | Item 3 | control contacts/relays, |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2401 | [11 empty] | Item 4 | cabling and conduit fom MSSB |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2402 | [11 empty] | Item 5 | and local power isolator. |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2403 | [11 empty] | Item 6 | This excludes supply and installation of AC manufacturers interface card where required. |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2404 | [11 empty] | Item 7 |  |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2405 | [11 empty] | Item 8 |  |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2406 | [11 empty] | Item 9 |  |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2407 | [11 empty] | Item 10 |  |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2408 | [11 empty] | Item 11 |  |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2409 | [11 empty] | Item 12 |  |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2410 | [11 empty] | Item 13 |  |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2411 | [11 empty] | Item 14 |  |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2412 | [11 empty] | Item 15 |  |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2413 | [11 empty] | Item 16 |  |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2414 | [11 empty] | Item 17 |  |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2415 | [11 empty] | Item 18 |  |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2416 | [11 empty] | Item 19 |  |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2417 | [11 empty] | Item 20 |  |  |  |  | 7 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2418 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2419 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2420 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2421 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2422 | [7 empty] | Electrical power supply and controls for ten (10) timeclock controlled energy recovery ventilators. Each includes supply and install of circuit breaker, timeclock controller, control contacts, cabling and conduit fom MSSB and local isolator. |  | ten | 10 | timeclock controlled energy recovery ventilators | Electrical power supply and controls for | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2423 | [11 empty] | Item 1 | circuit breaker, |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2424 | [11 empty] | Item 2 | timeclock controller, |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2425 | [11 empty] | Item 3 | control contacts, |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2426 | [11 empty] | Item 4 | cabling and conduit fom MSSB |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2427 | [11 empty] | Item 5 | and local isolator. |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2428 | [11 empty] | Item 6 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2429 | [11 empty] | Item 7 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2430 | [11 empty] | Item 8 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2431 | [11 empty] | Item 9 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2432 | [11 empty] | Item 10 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2433 | [11 empty] | Item 11 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2434 | [11 empty] | Item 12 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2435 | [11 empty] | Item 13 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2436 | [11 empty] | Item 14 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2437 | [11 empty] | Item 15 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2438 | [11 empty] | Item 16 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2439 | [11 empty] | Item 17 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2440 | [11 empty] | Item 18 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2441 | [11 empty] | Item 19 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2442 | [11 empty] | Item 20 |  |  |  |  | 10 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2443 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2444 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2445 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2446 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2447 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2448 | [7 empty] | Electrical power supply and controls cabling for two (2) central airconditioning controllers. Each includes supply and install of circuit breaker, power supply fom MSSB, interconnect controls cablingand display installThis excludes supply or commissioning od central controller. |  | two | 2 | central airconditioning controllers | Electrical power supply and controls cabling for | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2449 | [11 empty] | Item 1 | circuit breaker, |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2450 | [11 empty] | Item 2 | power supply fom MSSB, |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2451 | [11 empty] | Item 3 | interconnect controls cabling |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2452 | [11 empty] | Item 4 | and display install |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2453 | [11 empty] | Item 5 | This excludes supply or commissioning od central controller. |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2454 | [11 empty] | Item 6 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2455 | [11 empty] | Item 7 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2456 | [11 empty] | Item 8 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2457 | [11 empty] | Item 9 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2458 | [11 empty] | Item 10 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2459 | [11 empty] | Item 11 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2460 | [11 empty] | Item 12 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2461 | [11 empty] | Item 13 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2462 | [11 empty] | Item 14 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2463 | [11 empty] | Item 15 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2464 | [11 empty] | Item 16 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2465 | [11 empty] | Item 17 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2466 | [11 empty] | Item 18 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2467 | [11 empty] | Item 19 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2468 | [11 empty] | Item 20 |  |  |  |  | 2 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2469 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2470 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2471 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2472 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2473 | [7 empty] | Supply and install ninety-six (96) Typical apartment AC window interlocks ( no time delay). Each includes supply and install of Supply only of reed switch to be integrated into window frame by builders trade (2 per apartment), flush mounted junction box (1 per apartment)and controls cabling.Note we exclude AC interface card for window reed switches interface |  | ninety-six | 96 | Typical apartment AC window interlocks ( no time delay) | Supply and install | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2474 | [11 empty] | Item 1 | Supply only of reed switch to be integrated into window frame by builders trade (2 per apartment), |  |  |  | 192 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2475 | [11 empty] | Item 2 | flush mounted junction box (1 per apartment) |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2476 | [11 empty] | Item 3 | and controls cabling. |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2477 | [11 empty] | Item 4 | Note we exclude AC interface card for window reed switches interface |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2478 | [11 empty] | Item 5 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2479 | [11 empty] | Item 6 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2480 | [11 empty] | Item 7 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2481 | [11 empty] | Item 8 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2482 | [11 empty] | Item 9 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2483 | [11 empty] | Item 10 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2484 | [11 empty] | Item 11 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2485 | [11 empty] | Item 12 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2486 | [11 empty] | Item 13 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2487 | [11 empty] | Item 14 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2488 | [11 empty] | Item 15 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2489 | [11 empty] | Item 16 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2490 | [11 empty] | Item 17 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2491 | [11 empty] | Item 18 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2492 | [11 empty] | Item 19 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2493 | [11 empty] | Item 20 |  |  |  |  | 96 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2494 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2495 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2496 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2497 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2498 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2499 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2500 | [7 empty] | Supply and install fourteen (14) Common area door-AC interlocks ( with time delay). Each includes supply and install of reed switch integrated into door frame, flush mounted junction boxdelay timerand controls cabling.Note we exclude AC interface card for window reed switches interface |  | fourteen | 14 | Common area door-AC interlocks ( with time delay) | Supply and install | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2501 | [11 empty] | Item 1 | reed switch integrated into door frame, |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2502 | [11 empty] | Item 2 | flush mounted junction box |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2503 | [11 empty] | Item 3 | delay timer |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2504 | [11 empty] | Item 4 | and controls cabling. |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2505 | [11 empty] | Item 5 | Note we exclude AC interface card for window reed switches interface |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2506 | [11 empty] | Item 6 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2507 | [11 empty] | Item 7 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2508 | [11 empty] | Item 8 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2509 | [11 empty] | Item 9 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2510 | [11 empty] | Item 10 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2511 | [11 empty] | Item 11 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2512 | [11 empty] | Item 12 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2513 | [11 empty] | Item 13 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2514 | [11 empty] | Item 14 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2515 | [11 empty] | Item 15 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2516 | [11 empty] | Item 16 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2517 | [11 empty] | Item 17 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2518 | [11 empty] | Item 18 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2519 | [11 empty] | Item 19 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2520 | [11 empty] | Item 20 |  |  |  |  | 14 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2521 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2522 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2523 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2524 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2525 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2526 | [7 empty] | Supply and install twenty (20) common area window-AC interlocks ( no time delay). Each includes supply and install of micro switch integrated into window frame, flush mounted junction box,and controls cabling.Note we exclude AC interface card for window reed switches interface |  | twenty | 20 | common area window-AC interlocks ( no time delay) | Supply and install | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2527 | [11 empty] | Item 1 | micro switch integrated into window frame, |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2528 | [11 empty] | Item 2 | flush mounted junction box, |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2529 | [11 empty] | Item 3 | and controls cabling. |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2530 | [11 empty] | Item 4 | Note we exclude AC interface card for window reed switches interface |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2531 | [11 empty] | Item 5 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2532 | [11 empty] | Item 6 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2533 | [11 empty] | Item 7 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2534 | [11 empty] | Item 8 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2535 | [11 empty] | Item 9 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2536 | [11 empty] | Item 10 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2537 | [11 empty] | Item 11 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2538 | [11 empty] | Item 12 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2539 | [11 empty] | Item 13 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2540 | [11 empty] | Item 14 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2541 | [11 empty] | Item 15 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2542 | [11 empty] | Item 16 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2543 | [11 empty] | Item 17 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2544 | [11 empty] | Item 18 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2545 | [11 empty] | Item 19 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2546 | [11 empty] | Item 20 |  |  |  |  | 20 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2547 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2548 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2549 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2550 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2551 | [7 empty] | Electrical services for four (4) cold/freezer rooms. Each includes supply and install of internal lighting ( spec 12.10.2) and LED lighting to illuminate shelving behing insert doors (spec 12.3.6). For the freezer room(only), installation will include two powersupply circuits for underfloor heating.For the freezer room(only), installation will include powersupply for the door heater.Note: Powersupply for room and shelving lighting to be plovided in a junction box by electrical trade). Underfloor and door heating elements by others. |  | four | 4 | cold/freezer rooms | Electrical services for | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2552 | [11 empty] | Item 1 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2553 | [11 empty] | Item 2 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2554 | [11 empty] | Item 3 | internal lighting ( spec 12.10.2) |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2555 | [12 empty] | light switch complete with illuminated lamp | [8 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2556 | [11 empty] | Item 4 | and LED lighting to illuminate shelving behing insert doors (spec 12.3.6). |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2557 | [11 empty] | Item 5 | For the freezer room(only), installation will include two powersupply circuits for underfloor heating. |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2558 | [11 empty] | Item 6 | For the freezer room(only), installation will include powersupply for the door heater. |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2559 | [11 empty] | Item 7 | Note: Powersupply for room and shelving lighting to be plovided in a junction box by electrical trade). Underfloor and door heating elements by others. |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2560 | [11 empty] | Item 8 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2561 | [11 empty] | Item 9 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2562 | [11 empty] | Item 10 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2563 | [11 empty] | Item 11 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2564 | [11 empty] | Item 12 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2565 | [11 empty] | Item 13 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2566 | [11 empty] | Item 14 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2567 | [11 empty] | Item 15 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2568 | [11 empty] | Item 16 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2569 | [11 empty] | Item 17 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2570 | [11 empty] | Item 18 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2571 | [11 empty] | Item 19 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2572 | [11 empty] | Item 20 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2573 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2574 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2575 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2576 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2577 | [7 empty] | Electrical services for four (4) freezer refrigeration systems. Each includes supply and install of powersupply from MSSB to condenser set (including CB, contactors, wiring and local isolator),powersupply from MSSB to evaporator (including CB, contactors, wiring and local isolator)Installation (only) of refrigeration controller ( including power supply and interconnect controls cabling)Installation (only) of temperature probeFor freezer, installation includes powersupply from MSSB to evaporator heaters (including CB, contactors, wiring and local isolator)For freezer, installation includes powersupply from MSSB to evaporator heaters (including CB, contactors, wiring and local isolator)For freezer, installation includes proximity switch for freezer door ( spec 15.9.2)Commissioning of control panel and refrigeration systems is excluded.Supply of heaters is excluded. |  | four | 4 | freezer refrigeration systems | Electrical services for | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2578 | [11 empty] | Item 1 | powersupply from MSSB to condenser set (including CB, contactors, wiring and local isolator), |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2579 | [11 empty] | Item 2 | powersupply from MSSB to evaporator (including CB, contactors, wiring and local isolator) |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2580 | [11 empty] | Item 3 | Installation (only) of refrigeration controller ( including power supply and interconnect controls cabling) |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2581 | [11 empty] | Item 4 | Installation (only) of temperature probe |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2582 | [11 empty] | Item 5 | For freezer, installation includes powersupply from MSSB to evaporator heaters (including CB, contactors, wiring and local isolator) |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2583 | [11 empty] | Item 6 | For freezer, installation includes powersupply from MSSB to evaporator heaters (including CB, contactors, wiring and local isolator) |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2584 | [11 empty] | Item 7 | For freezer, installation includes proximity switch for freezer door ( spec 15.9.2) |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2585 | [11 empty] | Item 8 | Commissioning of control panel and refrigeration systems is excluded. |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2586 | [11 empty] | Item 9 | Supply of heaters is excluded. |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2587 | [11 empty] | Item 10 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2588 | [11 empty] | Item 11 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2589 | [11 empty] | Item 12 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2590 | [11 empty] | Item 13 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2591 | [11 empty] | Item 14 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2592 | [11 empty] | Item 15 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2593 | [11 empty] | Item 16 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2594 | [11 empty] | Item 17 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2595 | [11 empty] | Item 18 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2596 | [11 empty] | Item 19 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2597 | [11 empty] | Item 20 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2598 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2599 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2600 | [21 empty] | #N/A | [5 empty] | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2601 | [10 empty] | Number off systems | System Description | Major component ( included in cover letter description). Note as excluded/supply only/install at end only where not supply and install | Minor Components or internal notes ( not shown in cover letter) |  |  | QTY | Labour hrs ( per item) | A: Labour cost (per item) |  | B: Materials cost per item | #N/A |  |  |  |  | B: Materials cost per item | #N/A | [6 empty] | 0 | 0 | 0 | 0 | 0
2602 | [7 empty] | Electrical services for four (4) Mechanical services switchboard. Each includes supply and install of Main Isolators - Econtactorscircuit breakersbusbar and wiringthermographic testNote: Lamps and Auto/Off/Manual switches are excluded. |  | four | 4 | Mechanical services switchboard | Electrical services for | [5 empty] | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 1 | Main Isolators - E |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 2 | contactors |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 3 | circuit breakers |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 4 | busbar and wiring |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 5 | thermographic test |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 6 | Note: Lamps and Auto/Off/Manual switches are excluded. |  |  |  | 1 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 7 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 8 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 9 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 10 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 11 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 12 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 13 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 14 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 15 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 16 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 17 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 18 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 19 |  |  |  |  | 4 |  | #REF! |  |  | #N/A | [5 empty] | #N/A
[12 empty] | Item 20 |  |  |  |  | 4 |  | #REF!
0
0

## Sheet2
0 | Zero
1 | one
2 | two
3 | three
4 | four
5 | five
6 | six
7 | seven
8 | eight
9 | nine
10 | ten
11 | eleven
12 | twelve
13 | thirteen
14 | fourteen
15 | fifteen
16 | sixteen
17 | seventeen
18 | eighteen
19 | nineteen
20 | twenty
21 | twenty-one
22 | twenty-two
23 | twenty-three
24 | twenty-four
25 | twenty-five
26 | twenty-six
27 | twenty-seven
28 | twenty-eight
29 | twenty-nine
30 | thirty
31 | thirty-one
32 | thirty-two
33 | thirty-three
34 | thirty-four
35 | thirty-five
36 | thirty-six
37 | thirty-seven
38 | thirty-eight
39 | thirty-nine
40 | forty
41 | forty-one
42 | forty-two
43 | forty-three
44 | forty-four
45 | forty-five
46 | forty-six
47 | forty-seven
48 | forty-eight
49 | forty-nine
50 | fifty
51 | fifty-one
52 | fifty-two
53 | fifty-three
54 | fifty-four
55 | fifty-five
56 | fifty-six
57 | fifty-seven
58 | fifty-eight
59 | fifty-nine
60 | sixty
61 | sixty-one
62 | sixty-two
63 | sixty-three
64 | sixty-four
65 | sixty-five
66 | sixty-six
67 | sixty-seven
68 | sixty-eight
69 | sixty-nine
70 | seventy
71 | seventy-one
72 | seventy-two
73 | seventy-three
74 | seventy-four
75 | seventy-five
76 | seventy-six
77 | seventy-seven
78 | seventy-eight
79 | seventy-nine
80 | eighty
81 | eighty-one
82 | eighty-two
83 | eighty-three
84 | eighty-four
85 | eighty-five
86 | eighty-six
87 | eighty-seven
88 | eighty-eight
89 | eighty-nine
90 | ninety
91 | ninety-one
92 | ninety-two
93 | ninety-three
94 | ninety-four
95 | ninety-five
96 | ninety-six
97 | ninety-seven
98 | ninety-eight
99 | ninety-nine
100 | one hundred
101
102
103
104
105
106
107
108
109
110
111
112
113
114
115
116
117
118
119
120
121
122
123
124
125
126
127
128
129
130 | one hundred and thirty
131
132
133
134
135
136 | one hundred and thirty six
137
138
139
140
141
142
143
144
145
146
147
148
149
150
151

## Sheet3
Customers in-house electrician | interconnect cabling,
Customers in-house electrician | and local power isolator ( for Indoor unit).
Customers in-house electrician | proprietary air-conditioning controllers supply and installation.
Customers in-house electrician | Run signal controls cabling from each AC system adjacent to MSSB for run lights. Customers electrician to leave tails adjacent MSSB for Controlworks to connect.
Customers in-house electrician | Fault signal controls cabling from each AC system adjacent to MSSB for fault lights. Customers electrician to leave tails adjacent MSSB for Controlworks to connect.
AC system supplier | interface card for air-conditioning controllers for both run and fault indication.
Customers in-house electrician | Power cabling from MSSB to outdoor unit. Customers electrician to leave tails adjacent MSSB for Controlworks to connect.
0
connections of both controls and power cabling into MSSB,
testing of customer installed power cabling for compliance with AS3000 ( including polarity, insulation resistance, earth continuity and fault loop impedence),
Documented test results of final electrical systems and Form 16 certification.

## BACKEND
Electrical power supply and controls to | Unit Type | Power Supply | Facet | Interlocked with
| NULL | NULL | NULL | NULL
from | Fan | Local | Timeclock Control | Lighting Circuit
power supply |  | MSSB | Run On timer | Local Switch
Supply and install of power and controls |  |  | Interlock | Associated Unit
Power for system includes: |  |  | Mechanical Thermostat
Controls for system includes: |  |  | Reed Switch
Excludes: |  |  | Fire Shutdown
controls cabling, contactors/relays, run and fault lights, Auto/Off/On switch, controls enclosure, trefolyte labelling |  |  | Local switch & Run Status Light
, |  |  | BMS Provisions
This includes supply and install of power and controls.
commissioning/testing.
·
Excludes: No specific exclusions

## Build
Unit ID | QTY | Unit Type | Power Supply | Facet
1 | 4 | Fan | Local | Timeclock Control | Fire Shutdown | Interlock with Lighting Circuit | Reed Switch | BMS Provisions
2 | 1 | Fan | MSSB | Run On timer | Local switch & Run Status Light | Interlock with Associated Units | Mechanical Thermostat
3 | 6 | Fan | Local
4 | 7 | Fan | MSSB
5 | 8

## Power Supply
Power Supply |  |  | Power Supply | Controls | Notes | Exclusions
Local | cabling to | and control panel (from Builder's Electrician's isolator) and local isolator. | cabling to fan and control panel (from Builder's Electrician's isolator) and local isolator | commissioning/testing | Coordination Note: - Builders electrician: Please refer to our exclusions relating to local power supply | Supply of local power supply.
MSSB | CB and cabling to | from MSSB, and local isolator. | CB, cabling from MSSB, and local isolator. | commissioning/testing

## Facet
Facet | ToString | Power Supply | Controls | Notes | Exclusions
Timeclock Control | , Timeclock Control |  | adjustable timeclock controller,
Run On timer | , Run On timer | Run On Timer,
Interlock | , Interlock |  | interlock,
Mechanical Thermostat | , Mechanical Thermostat |  | interlock with Mechanical Thermostat,
Reed Switch | , Reed Switch |  | reed switch,
Fire Shutdown | , Fire Shutdown |  | fire relay for interface with fire trade, |  | Fire cabling from FIP.
Local switch & Run Status Light | , Local switch & Run Status Light |  | local switch, run on timer,
BMS Provisions | , BMS Provisions |  | current switch for fan status, BMS terminals for on/off control,
Interlock with Lighting Circuit | , Interlock with Lighting Circuit |  | Current switch for interlock with lighting circuit (note: current switch ensures clear demarcation between trades),
Interlock with Associated Units | , Interlock with Associated Units |  | Current switch for interlock with associated units (note: current switch ensures clear demarcation between trades),

## Unit
Unit
Fan
MSSB
PAC
Indoor DX Unit
Outdoor DX Unit
EDH
FCU Unit
Chiller

## Out
Unit ID | QTY | Unit Type | Power | Controls | Notes | Exclusions | Exclusions
1 | 4 | Electrical power supply and controls to 4 Fans from Local power supply with: , Timeclock Control, Fire Shutdown, Interlock with Lighting Circuit, Reed Switch, BMS Provisions | Power for system includes: cabling to Fan and control panel (from Builder's Electrician's isolator) and local isolator. | Controls for system includes: adjustable timeclock controller, fire relay for interface with fire trade, Current switch for interlock with lighting circuit (note: current switch ensures clear demarcation between trades), reed switch, current switch for fan status, BMS terminals for on/off control, and commissioning/testing. |  | Excludes: Supply of local power supply. | Excludes: Supply of local power supply.
2 | 1 | Electrical power supply and controls to 1 Fans from MSSB power supply with: , Run On timer, Local switch & Run Status Light, Interlock with Associated Units, Mechanical Thermostat | Power for system includes: Run On Timer, CB and cabling to Fan from MSSB, and local isolator. | Controls for system includes: local switch, run on timer, Current switch for interlock with associated units (note: current switch ensures clear demarcation between trades), interlock with Mechanical Thermostat, and commissioning/testing. |  | Excludes: | Excludes: No specific exclusions
3 | 6 | Electrical power supply and controls to 6 Fans from Local power supply | Power for system includes: cabling to Fan and control panel (from Builder's Electrician's isolator) and local isolator. | Controls for system includes: commissioning/testing. |  | Excludes: Supply of local power supply. | Excludes: Supply of local power supply.
4 | 7 | Electrical power supply and controls to 7 Fans from MSSB power supply | Power for system includes: CB and cabling to Fan from MSSB, and local isolator. | Controls for system includes: commissioning/testing. |  | Excludes: | Excludes: No specific exclusions

## Sheet8
Electrical power supply and controls to 4 Fans from Local power supply with: , Timeclock Control, Fire Shutdown, Interlock with Lighting Circuit, Reed Switch, BMS Provisions Power for system includes: cabling to Fan and control panel (from Builder's Electrician's isolator) and local isolator. Controls for system includes: adjustable timeclock controller, fire relay for interface with fire trade, Current switch for interlock with lighting circuit (note: current switch ensures clear demarcation between trades), reed switch, current switch for fan status, BMS terminals for on/off control, and commissioning/testing. Excludes: Supply of local power supply.
Electrical power supply and controls to 1 Fans from MSSB power supply with: , Run On timer, Local switch & Run Status Light, Interlock with Associated Units, Mechanical Thermostat Power for system includes: Run On Timer, CB and cabling to Fan from MSSB, and local isolator. Controls for system includes: local switch, run on timer, Current switch for interlock with associated units (note: current switch ensures clear demarcation between trades), interlock with Mechanical Thermostat, and commissioning/testing. Excludes: No specific exclusions
Electrical power supply and controls to 6 Fans from Local power supply Power for system includes: cabling to Fan and control panel (from Builder's Electrician's isolator) and local isolator. Controls for system includes: commissioning/testing. Excludes: Supply of local power supply.
Electrical power supply and controls to 7 Fans from MSSB power supply Power for system includes: CB and cabling to Fan from MSSB, and local isolator. Controls for system includes: commissioning/testing. Excludes: No specific exclusions
@